{"text_format":"1","workbook":"xlsx","n_sheets":8,"sheets":["Tabelle 1 - Pab_Indoor-Gehäuse","Tabelle 2 - Pab_Outdoor-Gehäuse","Tabelle 3 - Pv_Einbaugeräte","Tabelle 4 - Pv_Sammelschiene","Tabelle 4 - Pv_Sammelschiene1","Tabelle 5 - Pv_Kabel","Legende","Tabelle 101 - (61439-2, -3)"],"not_rendered":{"charts":0,"images":4,"macros":0,"external_links":0,"defined_names":20,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Tabelle 1 - Pab_Indoor-Gehäuse","index":0,"n_rows":476,"n_cols":17,"rows_kept":476,"cut":false,"hidden":false,"merged":[[0,15,2,15],[424,0,428,0],[424,1,428,1],[424,2,428,2],[424,5,428,5],[424,6,428,6],[433,0,436,0],[429,0,432,0],[429,1,432,1],[433,1,436,1],[429,2,432,2],[433,2,436,2],[433,5,436,5],[429,5,432,5],[429,6,432,6],[433,6,436,6],[414,0,418,0],[414,1,418,1],[414,2,418,2],[414,5,418,5],[414,6,418,6],[419,0,423,0],[419,1,423,1],[419,2,423,2],[419,5,423,5],[419,6,423,6],[404,0,408,0],[404,1,408,1],[404,2,408,2],[404,5,408,5],[404,6,408,6],[409,0,413,0],[409,1,413,1],[409,2,413,2],[409,5,413,5],[409,6,413,6],[394,0,398,0],[394,1,398,1],[394,2,398,2],[394,5,398,5],[394,6,398,6],[399,0,403,0],[399,1,403,1],[399,2,403,2],[399,5,403,5],[399,6,403,6],[384,0,388,0],[384,1,388,1],[384,2,388,2],[384,5,388,5],[384,6,388,6],[389,0,393,0],[389,1,393,1],[389,2,393,2],[389,5,393,5],[389,6,393,6],[378,0,378,6],[379,0,383,0],[379,1,383,1],[379,2,383,2],[379,5,383,5],[379,6,383,6],[343,6,377,6],[349,1,353,1],[349,2,353,2],[349,5,353,5],[355,1,359,1],[355,2,359,2],[355,5,359,5],[361,1,365,1],[361,2,365,2],[361,5,365,5],[308,0,342,0],[308,1,312,1],[308,2,312,2],[308,5,312,5],[338,1,342,1],[338,2,342,2],[338,5,342,5],[343,0,377,0],[343,1,347,1],[343,2,347,2],[343,5,347,5],[367,1,371,1],[367,2,371,2],[367,5,371,5],[373,1,377,1],[373,2,377,2],[373,5,377,5],[308,6,342,6],[314,1,318,1],[314,2,318,2],[314,5,318,5],[320,1,324,1],[320,2,324,2],[320,5,324,5],[326,1,330,1],[326,2,330,2],[326,5,330,5],[332,1,336,1],[332,2,336,2],[332,5,336,5],[197,6,237,6],[262,1,266,1],[262,2,266,2],[262,5,266,5],[209,5,213,5],[215,1,219,1],[215,2,219,2],[215,5,219,5],[221,1,225,1],[221,2,225,2],[221,5,225,5],[238,1,242,1],[238,2,242,2],[238,5,242,5],[250,1,254,1],[250,2,254,2],[256,1,260,1],[256,2,260,2],[256,5,260,5],[250,5,254,5],[244,1,248,1],[244,2,248,2],[244,5,248,5],[244,6,272,6],[197,0,237,0],[197,1,201,1],[197,2,201,2],[197,5,201,5],[203,1,207,1],[203,2,207,2],[203,5,207,5],[209,1,213,1],[209,2,213,2],[227,1,231,1],[227,2,231,2],[227,5,231,5],[233,1,237,1],[233,2,237,2],[233,5,237,5],[156,5,160,5],[156,6,196,6],[162,1,166,1],[162,2,166,2],[162,5,166,5],[168,1,172,1],[168,2,172,2],[186,1,190,1],[186,2,190,2],[186,5,190,5],[192,1,196,1],[192,2,196,2],[192,5,196,5],[168,5,172,5],[174,1,178,1],[174,2,178,2],[174,5,178,5],[180,1,184,1],[180,2,184,2],[180,5,184,5],[156,1,160,1],[156,2,160,2],[92,6,132,6],[98,1,102,1],[98,2,102,2],[98,5,102,5],[104,1,108,1],[104,2,108,2],[104,5,108,5],[110,1,114,1],[110,2,114,2],[110,5,114,5],[69,1,73,1],[69,2,73,2],[69,5,73,5],[87,1,91,1],[87,2,91,2],[87,5,91,5],[92,0,132,0],[92,1,96,1],[92,2,96,2],[92,5,96,5],[116,1,120,1],[116,2,120,2],[116,5,120,5],[122,1,126,1],[122,2,126,2],[122,5,126,5],[128,1,132,1],[128,2,132,2],[128,5,132,5],[45,5,48,5],[25,0,48,0],[25,1,28,1],[25,2,28,2],[25,5,28,5],[49,0,49,6],[50,0,50,6],[51,0,91,0],[51,1,55,1],[51,2,55,2],[51,5,55,5],[51,6,91,6],[57,1,61,1],[57,2,61,2],[57,5,61,5],[75,1,79,1],[75,2,79,2],[75,5,79,5],[81,1,85,1],[81,2,85,2],[81,5,85,5],[63,1,67,1],[63,2,67,2],[63,5,67,5],[8,1,10,1],[8,2,10,2],[8,5,10,5],[12,1,15,1],[25,6,48,6],[30,1,33,1],[30,2,33,2],[30,5,33,5],[35,1,38,1],[35,2,38,2],[12,2,15,2],[12,5,15,5],[17,1,20,1],[17,2,20,2],[17,5,20,5],[22,1,24,1],[22,2,24,2],[22,5,24,5],[35,5,38,5],[40,1,43,1],[40,2,43,2],[40,5,43,5],[45,1,48,1],[45,2,48,2],[4,5,6,5],[4,6,24,6],[273,0,307,0],[273,1,277,1],[273,2,277,2],[273,5,277,5],[279,1,283,1],[279,2,283,2],[279,5,283,5],[238,0,272,0],[133,0,155,0],[133,1,137,1],[133,2,137,2],[133,5,137,5],[139,1,143,1],[139,2,143,2],[139,5,143,5],[145,1,149,1],[145,2,149,2],[145,5,149,5],[151,1,155,1],[151,2,155,2],[151,5,155,5],[156,0,196,0],[1,7,1,11],[1,12,1,14],[0,0,0,14],[279,6,307,6],[285,1,289,1],[285,2,289,2],[285,5,289,5],[291,1,295,1],[291,2,295,2],[291,5,295,5],[297,1,301,1],[297,2,301,2],[297,5,301,5],[303,1,307,1],[303,2,307,2],[303,5,307,5],[268,1,272,1],[268,2,272,2],[268,5,272,5],[133,6,155,6],[3,0,3,6],[4,0,24,0],[4,1,6,1],[4,2,6,2]]}
["Tabelle Gehäuse-System: Angaben zur Wärmeberechnung gemäß DIN EN 61439-1, -2, -3",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Beschreibung"]
[null,null,null,null,null,null,null,"Abstrahlbare Verlustleistung Pab, W",null,null,null,null,"BxHxT für Wärmeberechung (ohne Sockel)\n[mm]"]
["Schrankart","Hersteller","Schutzart","Typ","B x H\n[mm]","Tiefe\n[mm]","Bemessungsstrom\nIn [A]","Beideseitg Frei, Wandaufstellung,\n20K 75% Gehäusehöhe","Einseitig abgedeckt, Wandaufstellung 20K 75% Gehäusehöhe","Beideseitig abgedeckt, Wandaufstellung\n20K 75% Gehäusehöhe","Beideseitg Frei Ruckwand Frei,\n20K 75% Gehäusehöhe","Beideseitg Frei, Wandaufstellung,\n20K 100% Gehäusehöhe","B "," H","Tiefe\n[mm]"]
["Installations-Flachverteiler"]
["UP/HW-Verteiler, modulare Lieferform, SK II Baureihe UL..  - Leergehäuse","ABN","IP30","UL13X","320 x 520",110,125,null,null,null,null,null,320,520,110]
[null,null,null,"UL23X","570 x 520",null,null,null,null,null,null,null,570,520,110]
[null,null,null,"UL33X","820 x 520",null,null,null,null,null,null,null,820,520,110]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,110]
[null,"ABN","IP30","UL14X","320 x 670",110,null,null,null,null,null,null,320,670,110]
[null,null,null,"UL24X","570 x 670",null,null,null,null,null,null,null,570,670,110]
[null,null,null,"UL34X","820 x 670",null,null,null,null,null,null,null,820,670,110]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,110]
[null,"ABN","IP30","UL15X","320 x 820",110,null,null,null,null,null,null,320,820,110]
[null,null,null,"UL25X","570 x 820",null,null,null,null,null,null,null,570,820,110]
[null,null,null,"UL35X","820 x 820",null,null,null,null,null,null,null,820,820,110]
[null,null,null,"UL45X","1070 x 820",null,null,null,null,null,null,null,1070,820,110]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,110]
[null,"ABN","IP30","UL16X","320 x 970",110,null,null,null,null,null,null,320,970,110]
[null,null,null,"UL26X","570 x 970",null,null,null,null,null,null,null,570,970,110]
[null,null,null,"UL36X","820 x 970",null,null,null,null,null,null,null,820,970,110]
[null,null,null,"UL46X","1070 x 970",null,null,null,null,null,null,null,1070,970,110]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,110]
[null,"ABN","IP30","UL17X","320 x 1120",110,null,null,null,null,null,null,320,1120,110]
[null,null,null,"UL27X","570 x 1120",null,null,null,null,null,null,null,570,1120,110]
[null,null,null,"UL37X","820 x 1120",null,null,null,null,null,null,null,820,1120,110,null,"ABNRM103"]
["AP-Verteiler, modulare Lieferform, SK II Baureihe RM..  - Leergehäuse","ABN","IP44","ABNRM103","300 x 500",160,250,null,null,null,null,null,300,500,160,"Feldverteiler AP Leer FB1 BH3 Volltür für 36TE REG T:160mm","ABNRM203"]
[null,null,null,"ABNRM203","550 x 500",null,null,null,null,null,null,null,550,500,160,"Feldverteiler AP Leer FB2 BH3 Volltür für 72TE REG T:160mm","ABNRM303"]
[null,null,null,"ABNRM303","800 x 500",null,null,null,null,null,null,null,800,500,160,"Feldverteiler AP Leer FB3 BH3 Volltür für 108TE REG T:160mm","ABNRM403"]
[null,null,null,"ABNRM403","1050 x 500",null,null,null,null,null,null,null,1050,500,160,"Feldverteiler AP Leer FB4 BH3 Volltür für 144TE REG T:160mm"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,160,null,"ABNRM104"]
[null,"ABN","IP44","ABNRM104","300 x 650",160,null,null,null,null,null,null,300,650,160,"Feldverteiler AP Leer FB1 BH4 Volltür für 48TE REG T:160mm","ABNRM204"]
[null,null,null,"ABNRM204","550 x 650",null,null,null,null,null,null,null,550,650,160,"Feldverteiler AP Leer FB2 BH4 Volltür für 96TE REG T:160mm","ABNRM304"]
[null,null,null,"ABNRM304","800 x 650",null,null,null,null,null,null,null,800,650,160,"Feldverteiler AP Leer FB3 BH4 Volltür für 144TE REG T:160mm","ABNRM404"]
[null,null,null,"ABNRM404","1050 x 650",null,null,null,null,null,null,null,1050,650,160,"Feldverteiler AP Leer FB4 BH4 Volltür für 192TE REG T:160mm"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,160,null,"ABNRM105"]
[null,"ABN","IP44","ABNRM105","300 x 800",160,null,null,null,null,null,null,300,800,160,"Feldverteiler AP Leer FB1 BH5 Volltür für 60TE REG T:160mm","ABNRM205"]
[null,null,null,"ABNRM205","550 x 800",null,null,null,null,null,null,null,550,800,160,"Feldverteiler AP Leer FB2 BH5 Volltür für 120TE REG T:160mm","ABNRM305"]
[null,null,null,"ABNRM305","800 x 800",null,null,null,null,null,null,null,800,800,160,"Feldverteiler AP Leer FB3 BH5 Volltür für 180TE REG T:160mm","ABNRM405"]
[null,null,null,"ABNRM405","1050 x 800",null,null,null,null,null,null,null,1050,800,160,"Feldverteiler AP Leer FB4 BH5 Volltür für 240TE REG T:160mm"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,160,null,"ABNRM106"]
[null,"ABN","IP44","ABNRM106","300 x 950",160,null,null,null,null,null,null,300,950,160,"Feldverteiler AP Leer FB1 BH6 Volltür für 72TE REG T:160mm","ABNRM206"]
[null,null,null,"ABNRM206","550 x 950",null,null,null,null,null,null,null,550,950,160,"Feldverteiler AP Leer FB2 BH6 Volltür für 144TE REG T:160mm","ABNRM306"]
[null,null,null,"ABNRM306","800 x 950",null,null,null,null,null,null,null,800,950,160,"Feldverteiler AP Leer FB3 BH6 Volltür für 216TE REG T:160mm","ABNRM406"]
[null,null,null,"ABNRM406","1050 x 950",null,null,null,null,null,null,null,1050,950,160,"Feldverteiler AP Leer FB4 BH6 Volltür für 288TE REG T:160mm"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,160,null,"ABNRM107"]
[null,"ABN","IP44","ABNRM107","300 x 1100",160,null,null,null,null,null,null,300,1100,160,"Feldverteiler AP Leer FB1 BH7 Volltür für 84TE REG T:160mm","ABNRM207"]
[null,null,null,"ABNRM207","550 x 1100",null,null,null,null,null,null,null,550,1100,160,"Feldverteiler AP Leer FB2 BH7 Volltür für 168TE REG T:160mm","ABNRM307"]
[null,null,null,"ABNRM307","800 x 1100",null,null,null,null,null,null,null,800,1100,160,"Feldverteiler AP Leer FB3 BH7 Volltür für 252TE REG T:160mm","ABNRM407"]
[null,null,null,"ABNRM407","1050 x 1100",null,null,null,null,null,null,null,1050,1100,160,"Feldverteiler AP Leer FB4 BH7 Volltür für 336TE REG T:160mm","ABNRM403"]
["Systemgehäuse"]
["Wandgehäuse",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"ABNRM104"]
["Wandgehäuse Baureihe ABNRV, SK I","ABN","IP44","ABNRV103","300 x 500",210,400,29,27,24,null,29,300,500,210,"Wandgehäuse geerdet IP44 BxHxT: 300x500x210mm","ABNRV103"]
[null,null,null,"ABNRV203","550 x 500",null,null,45,43,41,null,45,550,500,210,"Wandgehäuse geerdet IP44 BxHxT: 550x500x210mm","ABNRV203"]
[null,null,null,"ABNRV303","800 x 500",null,null,63,61,58,null,63,800,500,210,"Wandgehäuse geerdet IP44 BxHxT: 800x500x210mm","ABNRV303"]
[null,null,null,"ABNRV403","1050 x 500",null,null,80,78,75,null,80,1050,500,210,"Wandgehäuse geerdet IP44  BxHxT: 1050x500x210mm","ABNRV403"]
[null,null,null,"ABNRV503","1300 x 500",null,null,105,104,103,null,94,1300,500,210,"Wandgehäuse geerdet IP44 BxHxT: 1300x500x210mm","ABNRV503"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,210]
[null,"ABN","IP44","ABNRV104","300 x 650",210,null,35,32,29,null,35,300,650,210,"Wandgehäuse geerdet IP44 BxHxT: 300x650x210mm","ABNRV104"]
[null,null,null,"ABNRV204","550 x 650",null,null,53,50,47,null,53,550,650,210,"Wandgehäuse geerdet IP44 BxHxT: 550x650x210mm","ABNRV204"]
[null,null,null,"ABNRV304","800 x 650",null,null,73,70,67,null,73,800,650,210,"Wandgehäuse geerdet IP44 BxHxT: 800x650x210mm","ABNRV304"]
[null,null,null,"ABNRV404","1050 x 650",null,null,104,102,100,null,90,1050,650,210,"Wandgehäuse geerdet IP44 BxHxT: 1050x650x210mm","ABNRV404"]
[null,null,null,"ABNRV504","1300 x 650",null,null,126,124,123,null,111,1300,650,210,"Wandgehäuse geerdet IP44 BxHxT: 1300x650x210mm","ABNRV504"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,210]
[null,"ABN","IP44","ABNRV105","300 x 800",210,null,41,38,34,null,41,300,800,210,"Wandgehäuse geerdet IP44 BxHxT: 300x800x210mm","ABNRV105"]
[null,null,null,"ABNRV205","550 x 800",null,null,61,58,54,null,61,550,800,210,"Wandgehäuse geerdet IP44 BxHxT: 550x800x210mm","ABNRV205"]
[null,null,null,"ABNRV305","800 x 800",null,null,95,91,89,null,79,800,800,210,"Wandgehäuse geerdet IP44 BxHxT: 800x800x210mm","ABNRV305"]
[null,null,null,"ABNRV405","1050 x 800",null,null,121,118,115,null,103,1050,800,210,"Wandgehäuse geerdet IP44  BxHxT: 1050x800x210mm","ABNRV405"]
[null,null,null,"ABNRV505","1300 x 800",null,null,147,144,142,null,127,1300,800,210,"Wandgehäuse geerdet IP44 BxHxT: 1300x800x210mm","ABNRV505"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,210]
[null,"ABN","IP44","ABNRV106","300 x 950",210,null,47,43,39,null,47,300,950,210,"Wandgehäuse geerdet IP44 BxHxT: 300x950x210mm","ABNRV106"]
[null,null,null,"ABNRV206","550 x 950",null,null,69,65,61,null,69,550,950,210,"Wandgehäuse geerdet IP44 BxHxT: 550x950x210mm","ABNRV206"]
[null,null,null,"ABNRV306","800 x 950",null,null,107,103,100,null,88,800,950,210,"Wandgehäuse geerdet IP44 BxHxT: 800x950x210mm","ABNRV306"]
[null,null,null,"ABNRV406","1050 x 950",null,null,137,133,130,null,115,1050,950,210,"Wandgehäuse geerdet IP44 BxHxT: 1050x950x210mm","ABNRV406"]
[null,null,null,"ABNRV506","1300 x 950",null,null,166,163,161,null,142,1300,950,210,"Wandgehäuse geerdet IP44 BxHxT: 1300x950x210mm","ABNRV506"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,210]
[null,"ABN","IP44","ABNRV107","300 x 1100",210,null,54,49,44,null,54,300,1100,210,"Wandgehäuse geerdet IP44 BxHxT: 300x1100x210mm","ABNRV107"]
[null,null,null,"ABNRV207","550 x 1100",null,null,86,82,78,null,68,550,1100,210,"Wandgehäuse geerdet IP44 BxHxT: 550x1100x210mm","ABNRV207"]
[null,null,null,"ABNRV307","800 x 1100",null,null,119,114,111,null,97,800,1100,210,"Wandgehäuse geerdet IP44 BxHxT: 800x1100x210mm","ABNRV307"]
[null,null,null,"ABNRV407","1050 x 1100",null,null,152,148,144,null,126,1050,1100,210,"Wandgehäuse geerdet IP44 BxHxT: 1050x1100x210mm","ABNRV407"]
[null,null,null,"ABNRV507","1300 x 1100",null,null,185,181,178,null,156,1300,1100,210,"Wandgehäuse geerdet IP44 BxHxT: 1300x1100x210mm","ABNRV507"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,210]
[null,"ABN","IP44","ABNRV108","300 x 1250",210,null,60,54,49,null,60,300,1250,210,"Wandgehäuse geerdet IP44 BxHxT: 300x1250x210mm","ABNRV108"]
[null,null,null,"ABNRV208","550 x 1250",null,null,95,90,85,null,74,550,1250,210,"Wandgehäuse geerdet IP44 BxHxT: 550x1250x210mm","ABNRV208"]
[null,null,null,"ABNRV308","800 x 1250",null,null,130,125,121,null,105,800,1250,210,"Wandgehäuse geerdet IP44 BxHxT: 800x1250x210mm","ABNRV308"]
[null,null,null,"ABNRV408","1050 x 1250",null,null,167,162,158,null,137,1050,1250,210,"Wandgehäuse geerdet IP44 BxHxT: 1050x1250x210mm","ABNRV408"]
[null,null,null,"ABNRV508","1300 x 1250",null,null,203,199,196,null,169,1300,1250,210,"Wandgehäuse geerdet IP44 BxHxT: 1300x1250x210mm","ABNRV508"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,210]
[null,"ABN","IP44","ABNRV109","300 x 1400",210,null,66,60,54,null,66,300,1400,210,"Wandgehäuse geerdet IP44 BxHxT: 300x1400x210mm","ABNRV109"]
[null,null,null,"ABNRV209","550 x 1400",null,null,104,98,93,null,81,550,1400,210,"Wandgehäuse geerdet IP44 BxHxT: 550x1400x210mm","ABNRV209"]
[null,null,null,"ABNRV309","800 x 1400",null,null,142,136,131,null,112,800,1400,210,"Wandgehäuse geerdet IP44 BxHxT: 800x1400x210mm","ABNRV309"]
[null,null,null,"ABNRV409","1050 x 1400",null,null,181,176,172,null,147,1050,1400,210,"Wandgehäuse geerdet IP44 BxHxT: 1050x1400x210mm","ABNRV409"]
[null,null,null,"ABNRV509","1300 x 1400",null,null,221,216,213,null,182,1300,1400,210,"Wandgehäuse geerdet IP44 BxHxT: 1300x1400x210mm","ABNRV509"]
["Wandgehäuse Baureihe ABNRS, SK II","ABN","IP44","ABNRS103","300 x 500",210,400,29,27,24,null,29,300,500,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 300x500x210mm","ABNRS103"]
[null,null,null,"ABNRS203","550 x 500",null,null,45,43,41,null,45,550,500,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 550x500x210mm","ABNRS203"]
[null,null,null,"ABNRS303","800 x 500",null,null,63,61,58,null,63,800,500,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 800x500x210mm","ABNRS303"]
[null,null,null,"ABNRS403","1050 x 500",null,null,80,78,75,null,80,1050,500,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 1050x500x210mm","ABNRS403"]
[null,null,null,"ABNRS503","1300 x 500",null,null,105,104,103,null,94,1300,500,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 1300x500x210mm","ABNRS503"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,210]
[null,"ABN","IP44","ABNRS104","300 x 650",210,null,35,32,29,null,35,300,650,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 300x650x210mm","ABNRS104"]
[null,null,null,"ABNRS204","550 x 650",null,null,53,50,47,null,53,550,650,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 550x650x210mm","ABNRS204"]
[null,null,null,"ABNRS304","800 x 650",null,null,73,70,67,null,73,800,650,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 800x650x210mm","ABNRS304"]
[null,null,null,"ABNRS404","1050 x 650",null,null,104,102,100,null,90,1050,650,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 1050x650x210mm","ABNRS404"]
[null,null,null,"ABNRS504","1300 x 650",null,null,126,124,123,null,111,1300,650,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 1300x650x210mm","ABNRS504"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,210]
[null,"ABN","IP44","ABNRS105","300 x 800",210,null,41,38,34,null,41,300,800,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 300x800x210mm","ABNRS105"]
[null,null,null,"ABNRS205","550 x 800",null,null,61,58,54,null,61,550,800,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 550x800x210mm","ABNRS205"]
[null,null,null,"ABNRS305","800 x 800",null,null,95,91,89,null,79,800,800,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 800x800x210mm","ABNRS305"]
[null,null,null,"ABNRS405","1050 x 800",null,null,121,118,115,null,103,1050,800,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 1050x800x210mm","ABNRS405"]
[null,null,null,"ABNRS505","1300 x 800",null,null,147,144,142,null,127,1300,800,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 1300x800x210mm","ABNRS505"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,210]
[null,"ABN","IP44","ABNRS106","300 x 950",210,null,47,43,39,null,47,300,950,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 300x950x210mm","ABNRS106"]
[null,null,null,"ABNRS206","550 x 950",null,null,69,65,61,null,69,550,950,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 550x950x210mm","ABNRS206"]
[null,null,null,"ABNRS306","800 x 950",null,null,107,103,100,null,88,800,950,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 800x950x210mm","ABNRS306"]
[null,null,null,"ABNRS406","1050 x 950",null,null,137,133,130,null,115,1050,950,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 1050x950x210mm","ABNRS406"]
[null,null,null,"ABNRS506","1300 x 950",null,null,166,163,161,null,142,1300,950,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 1300x950x210mm","ABNRS506"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,210]
[null,"ABN","IP44","ABNRS107","300 x 1100",210,null,54,49,44,null,54,300,1100,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 300x1100x210mm","ABNRS107"]
[null,null,null,"ABNRS207","550 x 1100",null,null,86,82,78,null,68,550,1100,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 550x1100x210mm","ABNRS207"]
[null,null,null,"ABNRS307","800 x 1100",null,null,119,114,111,null,97,800,1100,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 800x1100x210mm","ABNRS307"]
[null,null,null,"ABNRS407","1050 x 1100",null,null,152,148,144,null,126,1050,1100,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 1050x1100x210mm","ABNRS407"]
[null,null,null,"ABNRS507","1300 x 1100",null,null,185,181,178,null,156,1300,1100,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 1300x1100x210mm","ABNRS507"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,210]
[null,"ABN","IP44","ABNRS108","300 x 1250",210,null,60,54,49,null,60,300,1250,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 300x1250x210mm","ABNRS108"]
[null,null,null,"ABNRS208","550 x 1250",null,null,95,90,85,null,74,550,1250,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 550x1250x210mm","ABNRS208"]
[null,null,null,"ABNRS308","800 x 1250",null,null,130,125,121,null,105,800,1250,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 800x1250x210mm","ABNRS308"]
[null,null,null,"ABNRS408","1050 x 1250",null,null,167,162,158,null,137,1050,1250,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 1050x1250x210mm","ABNRS408"]
[null,null,null,"ABNRS508","1300 x 1250",null,null,203,199,196,null,169,1300,1250,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 1300x1250x210mm","ABNRS508"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,210]
[null,"ABN","IP44","ABNRS109","300 x 1400",210,null,66,60,54,null,66,300,1400,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 300x1400x210mm","ABNRS109"]
[null,null,null,"ABNRS209","550 x 1400",null,null,104,98,93,null,81,550,1400,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 550x1400x210mm","ABNRS209"]
[null,null,null,"ABNRS309","800 x 1400",null,null,142,136,131,null,112,800,1400,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 800x1400x210mm","ABNRS309"]
[null,null,null,"ABNRS409","1050 x 1400",null,null,181,176,172,null,147,1050,1400,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 1050x1400x210mm","ABNRS409"]
[null,null,null,"ABNRS509","1300 x 1400",null,null,221,216,213,null,182,1300,1400,210,"Wandgehäuse schutzisoliert IP44 BxHxT: 1300x1400x210mm ","ABNRS509"]
["Wandgehäuse Baureihe ABNRP, SK II","ABN","IP54","ABNRP103","300 x 500",210,400,29,27,24,null,29,300,500,210,"Wandgehäuse schutzisoliert IP54 BxHxT: 300x500x210mm","ABNRP103"]
[null,null,null,"ABNRP203","550 x 500",null,null,45,43,41,null,45,550,500,210,"Wandgehäuse schutzisoliert IP54 BxHxT: 550x500x210mm","ABNRP203"]
[null,null,null,"ABNRP303","800 x 500",null,null,63,61,58,null,63,800,500,210,"Wandgehäuse schutzisoliert IP54 BxHxT: 800x500x210mm","ABNRP303"]
[null,null,null,"ABNRP403","1050 x 500",null,null,80,78,75,null,80,1050,500,210,"Wandgehäuse schutzisoliert IP54 BxHxT: 1050x500x210mm","ABNRP403"]
[null,null,null,"ABNRP503","1300 x 500",null,null,105,104,103,null,94,1300,500,210,"Wandgehäuse schutzisoliert IP54 BxHxT: 1300x500x210mm","ABNRP503"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,210]
[null,"ABN","IP54","ABNRP106","300 x 950",210,null,47,43,39,null,47,300,950,210,"Wandgehäuse schutzisoliert IP54 BxHxT: 300x950x210mm","ABNRP106"]
[null,null,null,"ABNRP206","550 x 950",null,null,69,65,61,null,69,550,950,210,"Wandgehäuse schutzisoliert IP54 BxHxT: 550x950x210mm","ABNRP206"]
[null,null,null,"ABNRP306","800 x 950",null,null,107,103,100,null,88,800,950,210,"Wandgehäuse schutzisoliert IP54 BxHxT: 800x950x210mm","ABNRP306"]
[null,null,null,"ABNRP406","1050 x 950",null,null,137,133,130,null,115,1050,950,210,"Wandgehäuse schutzisoliert IP54 BxHxT: 1050x950x210mm","ABNRP406"]
[null,null,null,"ABNRP506","1300 x 950",null,null,166,163,161,null,142,1300,950,210,"Wandgehäuse schutzisoliert IP54 BxHxT: 1300x950x210mm","ABNRP506"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,210]
[null,"ABN","IP54","ABNRP107","300 x 1100",210,null,54,49,44,null,54,300,1100,210,"Wandgehäuse schutzisoliert IP54 BxHxT: 300x1100x210mm","ABNRP107"]
[null,null,null,"ABNRP207","550 x 1100",null,null,86,82,78,null,68,550,1100,210,"Wandgehäuse schutzisoliert IP54 BxHxT: 550x1100x210mm","ABNRP207"]
[null,null,null,"ABNRP307","800 x 1100",null,null,119,114,111,null,97,800,1100,210,"Wandgehäuse schutzisoliert IP54 BxHxT: 800x1100x210mm","ABNRP307"]
[null,null,null,"ABNRP407","1050 x 1100",null,null,152,148,144,null,126,1050,1100,210,"Wandgehäuse schutzisoliert IP54 BxHxT: 1050x1100x210mm","ABNRP407"]
[null,null,null,"ABNRP507","1300 x 1100",null,null,185,181,178,null,156,1300,1100,210,"Wandgehäuse schutzisoliert IP54 BxHxT: 1300x1100x210mm","ABNRP507"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,210]
[null,"ABN","IP54","ABNRP109","300 x 1400",210,null,66,60,54,null,66,300,1400,210,"Wandgehäuse schutzisoliert IP54 BxHxT: 300x1400x210mm","ABNRP109"]
[null,null,null,"ABNRP209","550 x 1400",null,null,104,98,93,null,81,550,1400,210,"Wandgehäuse schutzisoliert IP54 BxHxT: 550x1400x210mm","ABNRP209"]
[null,null,null,"ABNRP309","800 x 1400",null,null,142,136,131,null,112,800,1400,210,"Wandgehäuse schutzisoliert IP54 BxHxT: 800x1400x210mm","ABNRP309"]
[null,null,null,"ABNRP409","1050 x 1400",null,null,181,176,172,null,147,1050,1400,210,"Wandgehäuse schutzisoliert IP54 BxHxT: 1050x1400x210mm","ABNRP409"]
[null,null,null,"ABNRP509","1300 x 1400",null,null,221,216,213,null,182,1300,1400,210,"Wandgehäuse schutzisoliert IP54 BxHxT: 1300x1400x210mm","ABNRP509"]
["Wandgehäuse Baureihe SE, SK I","ABN","IP54","SE13","300 x 500",225,400,30,28,25,null,30,300,500,225,"Wandgehäuse geerdet 300x500x225mm IP54","SE13"]
[null,null,null,"SE23","550 x 500",null,null,47,45,42,null,47,550,500,225,"Wandgehäuse geerdet 550x500x225mm IP54","SE23"]
[null,null,null,"SE33","800 x 500",null,null,65,63,60,null,65,800,500,225,"Wandgehäuse geerdet 800x500x225mm IP54","SE33"]
[null,null,null,"SE43","1050 x 500",null,null,81,80,78,null,80,1050,500,225,"Wandgehäuse geerdet 1050x500x225mm IP54","SE43"]
[null,null,null,"SE53","1300 x 500",null,null,110,108,107,null,98,1300,500,225,"Wandgehäuse geerdet 1300x500x225mm IP54","SE53"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,225]
[null,"ABN","IP54","SE14","300 x 650",225,null,37,34,30,null,37,300,650,225,"Wandgehäuse geerdet 300x650x225mm IP54","SE14"]
[null,null,null,"SE24","550 x 650",null,null,55,52,49,null,55,550,650,225,"Wandgehäuse geerdet 550x650x225mm IP54","SE24"]
[null,null,null,"SE34","800 x 650",null,null,76,73,69,null,76,800,650,225,"Wandgehäuse geerdet 800x650x225mm IP54","SE34"]
[null,null,null,"SE44","1050 x 650",null,null,108,106,104,null,94,1050,650,225,"Wandgehäuse geerdet 1050x650x225mm IP54","SE44"]
[null,null,null,"SE54","1300 x 650",null,null,131,129,127,null,115,1300,650,225,"Wandgehäuse geerdet 1300x650x225mm IP54","SE54"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,225]
[null,"ABN","IP54","SE15","300 x 800",225,null,43,39,35,null,43,300,800,225,"Wandgehäuse geerdet 300x800x225mm IP54","SE15"]
[null,null,null,"SE25","550 x 800",null,null,64,60,56,null,64,550,800,225,"Wandgehäuse geerdet 550x800x225mm IP54","SE25"]
[null,null,null,"SE35","800 x 800",null,null,99,95,92,null,84,800,800,225,"Wandgehäuse geerdet 800x800x225mm IP54","SE35"]
[null,null,null,"SE45","1050 x 800",null,null,126,122,119,null,108,1050,800,225,"Wandgehäuse geerdet 1050x800x225mm IP54","SE45"]
[null,null,null,"SE55","1300 x 800",null,null,152,149,147,null,132,1300,800,225,"Wandgehäuse geerdet 1300x800x225mm IP54","SE55"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,225]
[null,"ABN","IP54","SE16","300 x 950",225,null,50,44,40,null,50,300,950,225,"Wandgehäuse geerdet 300x950x225mm IP54","SE16"]
[null,null,null,"SE26","550 x 950",null,null,72,68,63,null,66,550,950,225,"Wandgehäuse geerdet 550x950x225mm IP54","SE26"]
[null,null,null,"SE36","800 x 950",null,null,112,107,104,null,93,800,950,225,"Wandgehäuse geerdet 800x950x225mm IP54","SE36"]
[null,null,null,"SE46","1050 x 950",null,null,142,138,135,null,120,1050,950,225,"Wandgehäuse geerdet 1050x950x225mm IP54","SE46"]
[null,null,null,"SE56","1300 x 950",null,null,172,168,166,null,148,1300,950,225,"Wandgehäuse geerdet 1300x950x225mm IP54","SE56"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,225]
[null,"ABN","IP54","SE17","300 x 1100",225,null,56,51,46,null,56,300,1100,225,"Wandgehäuse geerdet 300x1100x225mm IP54","SE17"]
[null,null,null,"SE27","550 x 1100",null,null,91,85,81,null,72,550,1100,225,"Wandgehäuse geerdet 550x1100x225mm IP54","SE27"]
[null,null,null,"SE37","800 x 1100",null,null,124,119,115,null,101,800,1100,225,"Wandgehäuse geerdet 800x1100x225mm IP54","SE37"]
[null,null,null,"SE47","1050 x 1100",null,null,158,153,149,null,132,1050,1100,225,"Wandgehäuse geerdet 1050x1100x225mm IP54","SE47"]
[null,null,null,"SE57","1300 x 1100",null,null,192,187,184,null,162,1300,1100,225,"Wandgehäuse geerdet 1300x1100x225mm IP54","SE57"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,225]
[null,"ABN","IP54","SE18","300 x 1250",225,null,62,56,51,null,62,300,1250,225,"Wandgehäuse geerdet 300x1250x225mm IP54","SE18"]
[null,null,null,"SE28","550 x 1250",null,null,100,94,88,null,78,550,1250,225,"Wandgehäuse geerdet 550x1250x225mm IP54","SE28"]
[null,null,null,"SE38","800 x 1250",null,null,136,130,125,null,110,800,1250,225,"Wandgehäuse geerdet 800x1250x225mm IP54","SE38"]
[null,null,null,"SE48","1050 x 1250",null,null,173,168,163,null,143,1050,1250,225,"Wandgehäuse geerdet 1050x1250x225mm IP54","SE48"]
[null,null,null,"SE58","1300 x 1250",null,null,210,205,202,null,176,1300,1250,225,"Wandgehäuse geerdet 1300x1250x225mm IP54","SE58"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,225]
[null,"ABN","IP54","SE19","300 x 1400",225,null,68,62,55,null,68,300,1400,225,"Wandgehäuse geerdet 300x1400x225mm IP54","SE19"]
[null,null,null,"SE29","550 x 1400",null,null,108,101,95,null,84,550,1400,225,"Wandgehäuse geerdet 550x1400x225mm IP54","SE29"]
[null,null,null,"SE39","800 x 1400",null,null,148,141,136,null,118,800,1400,225,"Wandgehäuse geerdet 800x1400x225mm IP54","SE39"]
[null,null,null,"SE49","1050 x 1400",null,null,188,182,177,null,153,1050,1400,225,"Wandgehäuse geerdet 1050x1400x225mm IP54","SE49"]
[null,null,null,"SE59","1300 x 1400",null,null,228,223,219,null,190,1300,1400,225,"Wandgehäuse geerdet 1300x1400x225mm IP54","SE59"]
["Wandgehäuse Baureihe SP, SK II","ABN","IP54","SP13","300 x 500",225,400,30,28,25,null,30,300,500,225,"Wandgehäuse schutzisoliert 300x502x225mm IP54","SP13"]
[null,null,null,"SP23","550 x 500",null,null,47,45,42,null,47,550,500,225,"Wandgehäuse schutzisoliert 550x502x225mm IP54","SP23"]
[null,null,null,"SP33","800 x 500",null,null,65,63,60,null,65,800,500,225,"Wandgehäuse schutzisoliert 800x502x225mm IP54","SP33"]
[null,null,null,"SP43","1050 x 500",null,null,81,80,78,null,80,1050,500,225,"Wandgehäuse schutzisoliert 1050x502x225mm IP54","SP43"]
[null,null,null,"SP53","1300 x 500",null,null,110,108,107,null,98,1300,500,225,"Wandgehäuse schutzisoliert 1300x502x225mm IP54","SP53"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,225]
[null,"ABN","IP54","SP14","300 x 650",225,null,37,34,30,null,37,300,650,225,"Wandgehäuse schutzisoliert 300x650x225mm IP54","SP14"]
[null,null,null,"SP24","550 x 650",null,null,55,52,49,null,55,550,650,225,"Wandgehäuse schutzisoliert 550x650x225mm IP54","SP24"]
[null,null,null,"SP34","800 x 650",null,null,76,73,69,null,76,800,650,225,"Wandgehäuse schutzisoliert 800x650x225mm IP54","SP34"]
[null,null,null,"SP44","1050 x 650",null,null,108,106,104,null,94,1050,650,225,"Wandgehäuse schutzisoliert 1050x650x225mm IP54","SP44"]
[null,null,null,"SP54","1300 x 650",null,null,131,129,127,null,115,1300,650,225,"Wandgehäuse schutzisoliert 1300x650x225mm IP54","SP54"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,225]
[null,"ABN","IP54","SP15","300 x 800",225,null,43,39,35,null,43,300,800,225,"Wandgehäuse schutzisoliert 300x800x225mm IP54","SP15"]
[null,null,null,"SP25","550 x 800",null,null,64,60,56,null,64,550,800,225,"Wandgehäuse schutzisoliert 550x800x225mm IP54","SP25"]
[null,null,null,"SP35","800 x 800",null,null,99,95,92,null,84,800,800,225,"Wandgehäuse schutzisoliert 800x800x225mm IP54","SP35"]
[null,null,null,"SP45","1050 x 800",null,null,126,122,119,null,108,1050,800,225,"Wandgehäuse schutzisoliert 1050x800x225mm IP54","SP45"]
[null,null,null,"SP55","1300 x 800",null,null,152,149,147,null,132,1300,800,225,"Wandgehäuse schutzisoliert 1300x800x225mm IP54","SP55"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,225]
[null,"ABN","IP54","SP16","300 x 950",225,null,50,44,40,null,50,300,950,225,"Wandgehäuse schutzisoliert 300x950x225mm IP54","SP16"]
[null,null,null,"SP26","550 x 950",null,null,72,68,63,null,66,550,950,225,"Wandgehäuse schutzisoliert 550x950x225mm IP54","SP26"]
[null,null,null,"SP36","800 x 950",null,null,112,107,104,null,93,800,950,225,"Wandgehäuse schutzisoliert 800x950x225mm IP54","SP36"]
[null,null,null,"SP46","1050 x 950",null,null,142,138,135,null,120,1050,950,225,"Wandgehäuse schutzisoliert 1050x950x225mm IP54","SP46"]
[null,null,null,"SP56","1300 x 950",null,null,172,168,166,null,148,1300,950,225,"Wandgehäuse schutzisoliert 1300x950x225mm IP54","SP56"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,225]
[null,"ABN","IP54","SP17","300 x 1100",225,null,56,51,46,null,56,300,1100,225,"Wandgehäuse schutzisoliert 300x1100x225mm IP54","SP17"]
[null,null,null,"SP27","550 x 1100",null,null,91,85,81,null,72,550,1100,225,"Wandgehäuse schutzisoliert 550x1100x225mm IP54","SP27"]
[null,null,null,"SP37","800 x 1100",null,null,124,119,115,null,101,800,1100,225,"Wandgehäuse schutzisoliert 800x1100x225mm IP54","SP37"]
[null,null,null,"SP47","1050 x 1100",null,null,158,153,149,null,132,1050,1100,225,"Wandgehäuse schutzisoliert 1050x1100x225mm IP54","SP47"]
[null,null,null,"SP57","1300 x 1100",null,null,192,187,184,null,162,1300,1100,225,"Wandgehäuse schutzisoliert 1300x1100x225mm IP54","SP57"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,225]
[null,"ABN","IP54","SP18","300 x 1250",225,null,62,56,51,null,62,300,1250,225,"Wandgehäuse schutzisoliert 300x1250x225mm IP54","SP18"]
[null,null,null,"SP28","550 x 1250",null,null,100,94,88,null,78,550,1250,225,"Wandgehäuse schutzisoliert 550x1250x225mm IP54","SP28"]
[null,null,null,"SP38","800 x 1250",null,null,136,130,125,null,110,800,1250,225,"Wandgehäuse schutzisoliert 800x1250x225mm IP54","SP38"]
[null,null,null,"SP48","1050 x 1250",null,null,173,168,163,null,143,1050,1250,225,"Wandgehäuse schutzisoliert 1050x1250x225mm IP54","SP48"]
[null,null,null,"SP58","1300 x 1250",null,null,210,205,202,null,176,1300,1250,225,"Wandgehäuse schutzisoliert 1300x1250x225mm IP54","SP58"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,225]
[null,"ABN","IP54","SP19","300 x 1400",225,null,68,62,55,null,68,300,1400,225,"Wandgehäuse schutzisoliert 300x1400x225mm IP54","SP19"]
[null,null,null,"SP29","550 x 1400",null,null,108,101,95,null,84,550,1400,225,"Wandgehäuse schutzisoliert 550x1400x225mm IP54","SP29"]
[null,null,null,"SP39","800 x 1400",null,null,148,141,136,null,118,800,1400,225,"Wandgehäuse schutzisoliert 800x1400x225mm IP54","SP39"]
[null,null,null,"SP49","1050 x 1400",null,null,188,182,177,null,153,1050,1400,225,"Wandgehäuse schutzisoliert 1050x1400x225mm IP54","SP49"]
[null,null,null,"SP59","1300 x 1400",null,null,228,223,219,null,190,1300,1400,225,"Wandgehäuse schutzisoliert 1300x1400x225mm IP54","SP59"]
["Wandgehäuse Baureihe NF..E, SK I","ABN","IP55","NF14E","340 x 690",280,null,46,42,38,null,46,340,690,280,"Wandgehäuse geerdet 340x690x280mm IP55","NF14E"]
[null,null,null,"NF24E","590 x 690",null,null,66,62,58,null,66,590,690,280,"Wandgehäuse geerdet 590x690x280mm IP55","NF24E"]
[null,null,null,"NF34E","840 x 690",null,null,103,98,95,null,89,840,690,280,"Wandgehäuse geerdet 840x690x280mm IP55","NF34E"]
[null,null,null,"NF44E","1090 x 690",null,null,128,124,121,null,112,1090,690,280,"Wandgehäuse geerdet 1090x690x280mm IP55","NF44E"]
[null,null,null,"NF54E","1340 x 690",null,null,153,149,147,null,135,1340,690,280,"Wandgehäuse geerdet 1340x690x280mm IP55","NF54E"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,280]
[null,"ABN","IP55","NF15E","340 x 840",280,630,53,48,43,null,53,340,840,280,"Wandgehäuse geerdet 340x840x280mm IP55","NF15E"]
[null,null,null,"NF25E","590 x 840",null,null,88,82,76,null,74,590,840,280,"Wandgehäuse geerdet 590x840x280mm IP55","NF25E"]
[null,null,null,"NF35E","840 x 840",null,null,118,113,108,null,100,840,840,280,"Wandgehäuse geerdet 840x840x280mm IP55","NF35E"]
[null,null,null,"NF45E","1090 x 840",null,null,147,142,138,null,127,1090,840,280,"Wandgehäuse geerdet 1090x1090x280mm IP55","NF45E"]
[null,null,null,"NF55E","1340 x 840",null,null,176,171,168,null,154,1340,840,280,"Wandgehäuse geerdet 1340x840x280mm IP55","NF55E"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,280]
[null,"ABN","IP55","NF16E","340 x 990",280,null,61,55,49,null,61,340,990,280,"Wandgehäuse geerdet 340x990x280mm IP55","NF16E"]
[null,null,null,"NF26E","590 x 990",null,null,99,92,85,null,81,590,990,280,"Wandgehäuse geerdet 590x990x280mm IP55","NF26E"]
[null,null,null,"NF36E","840 x 990",null,null,132,126,121,null,111,840,990,280,"Wandgehäuse geerdet 840x990x280mm IP55","NF36E"]
[null,null,null,"NF46E","1090 x 990",null,null,165,159,155,null,141,1090,990,280,"Wandgehäuse geerdet 1090x990x280mm IP55","NF46E"]
[null,null,null,"NF56E","1340 x 990",null,null,197,192,188,null,171,1340,990,280,"Wandgehäuse geerdet 1340x990x280mm IP55","NF56E"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,280]
[null,"ABN","IP55","NF17E","340 x 1140",280,null,68,62,55,null,68,340,1140,280,"Wandgehäuse geerdet 340x1140x280mm IP55","NF17E"]
[null,null,null,"NF27E","590 x 1140",null,null,110,103,97,null,89,590,1140,280,"Wandgehäuse geerdet 590x1140x280mm IP55","NF27E"]
[null,null,null,"NF37E","840 x 1140",null,null,146,139,134,null,121,840,1140,280,"Wandgehäuse geerdet 840x1140x280mm IP55","NF37E"]
[null,null,null,"NF47E","1090 x 1140",null,null,182,176,171,null,154,1090,1140,280,"Wandgehäuse geerdet 1090x1140x280mm IP55","NF47E"]
[null,null,null,"NF57E","1340 x 1140",null,null,219,213,208,null,187,1340,1140,280,"Wandgehäuse geerdet 1340x1140x280mm IP55","NF57E"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,280]
[null,"ABN","IP55","NF18E","340 x 1290",280,null,82,73,67,null,64,340,1290,280,"Wandgehäuse geerdet 340x1290x280mm IP55","NF18E"]
[null,null,null,"NF28E","590 x 1290",null,null,120,112,105,null,96,590,1290,280,"Wandgehäuse geerdet 590x1290x280mm IP55","NF28E"]
[null,null,null,"NF38E","840 x 1290",null,null,159,152,145,null,131,840,1290,280,"Wandgehäuse geerdet 840x1290x280mm IP55","NF38E"]
[null,null,null,"NF48E","1090 x 1290",null,null,199,192,186,null,167,1090,1290,280,"Wandgehäuse geerdet 1090x1290x280mm IP55","NF48E"]
[null,null,null,"NF58E","1340 x 1290",null,null,239,232,227,null,203,1340,1290,280,"Wandgehäuse geerdet 1340x1290x280mm IP55","NF58E"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,280]
[null,"ABN","IP55","NF19E","340 x 1440",280,null,91,82,74,null,70,340,1440,280,"Wandgehäuse geerdet 340x1440x280mm IP55","NF19E"]
[null,null,null,"NF29E","590 x 1440",null,null,130,121,114,null,103,590,1440,280,"Wandgehäuse geerdet 590x1440x280mm IP55","NF29E"]
[null,null,null,"NF39E","840 x 1440",null,null,172,164,157,null,140,840,1440,280,"Wandgehäuse geerdet 840x1440x280mm IP55","NF39E"]
[null,null,null,"NF49E","1090 x 1440",null,null,216,208,201,null,179,1090,1440,280,"Wandgehäuse geerdet 1090x1440x280mm IP55","NF49E"]
[null,null,null,"NF59E","1340 x 1440",null,null,259,252,246,null,218,1340,1440,280,"Wandgehäuse geerdet 1340x1440x280mm IP55","NF59E"]
["Wandgehäuse Baureihe NF..E, SK I","ABN","IP55","NF14P","340 x 690",280,null,46,42,38,null,46,340,690,280,"Wandgehäuse schutzisoliert 340x690x280mm IP55","NF14P"]
[null,null,null,"NF24P","590 x 690",null,null,66,62,58,null,66,590,690,280,"Wandgehäuse schutzisoliert 590x690x280mm IP55","NF24P"]
[null,null,null,"NF34P","840 x 690",null,null,103,98,95,null,89,840,690,280,"Wandgehäuse schutzisoliert 840x690x280mm IP55","NF34P"]
[null,null,null,"NF44P","1090 x 690",null,null,128,124,121,null,112,1090,690,280,"Wandgehäuse schutzisoliert 1090x690x280mm IP55","NF44P"]
[null,null,null,"NF54P","1340 x 690",null,null,153,149,147,null,135,1340,690,280,"Wandgehäuse schutzisoliert 1340x690x280mm IP55","NF54P"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,280]
[null,"ABN","IP55","NF15P","340 x 690",280,630,53,48,43,null,53,340,690,280,"Wandgehäuse schutzisoliert IP55 BxHxT: 340x840x280mm","NF15P"]
[null,null,null,"NF25P","590 x 690",null,null,88,82,76,null,74,590,690,280,"Wandgehäuse schutzisoliert IP55 BxHxT: 590x840x280mm","NF25P"]
[null,null,null,"NF35P","840 x 690",null,null,118,113,108,null,100,840,690,280,"Wandgehäuse schutzisoliert IP55 BxHxT: 840x840x280mm","NF35P"]
[null,null,null,"NF45P","1090 x 690",null,null,147,142,138,null,127,1090,690,280,"Wandgehäuse schutzisoliert IP55 BxHxT: 1090x840x280mm","NF45P"]
[null,null,null,"NF55P","1340 x 690",null,null,176,171,168,null,154,1340,690,280,"Wandgehäuse schutzisoliert IP55 BxHxT: 1340x840x280mm","NF55P"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,280]
[null,"ABN","IP55","NF16P","340 x 990",280,null,61,55,49,null,61,340,990,280,"Wandgehäuse schutzisoliert IP55 BxHxT: 340x990x280mm","NF16P"]
[null,null,null,"NF26P","590 x 990",null,null,99,92,85,null,81,590,990,280,"Wandgehäuse schutzisoliert 590x990x280mm IP55","NF26P"]
[null,null,null,"NF36P","840 x 990",null,null,132,126,121,null,111,840,990,280,"Wandgehäuse schutzisoliert 840x990x280mm IP55","NF36P"]
[null,null,null,"NF46P","1090 x 990",null,null,165,159,155,null,141,1090,990,280,"Wandgehäuse schutzisoliert 1090x990x280mm IP55","NF46P"]
[null,null,null,"NF56P","1340 x 990",null,null,197,192,188,null,171,1340,990,280,"Wandgehäuse schutzisoliert IP55 BxHxT: 1340x990x280mm","NF56P"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,280]
[null,"ABN","IP55","NF17P","340 x 1140",280,null,68,62,55,null,68,340,1140,280,"Wandgehäuse schutzisoliert IP55 BxHxT: 340x1140x280mm","NF17P"]
[null,null,null,"NF27P","590 x 1140",null,null,110,103,97,null,89,590,1140,280,"Wandgehäuse schutzisoliert 590x1140x280mm IP55","NF27P"]
[null,null,null,"NF37P","840 x 1140",null,null,146,139,134,null,121,840,1140,280,"Wandgehäuse schutzisoliert 840x1140x280mm IP55","NF37P"]
[null,null,null,"NF47P","1090 x 1140",null,null,182,176,171,null,154,1090,1140,280,"Wandgehäuse schutzisoliert 1090x1140x280mm IP55","NF47P"]
[null,null,null,"NF57P","1340 x 1140",null,null,219,213,208,null,187,1340,1140,280,"Wandgehäuse schutzisoliert 1340x1140x280mm IP55","NF57P"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,280]
[null,"ABN","IP55","NF18P","340 x 1290",280,null,82,73,67,null,64,340,1290,280,"Wandgehäuse schutzisoliert IP55 BxHxT: 340x1290x280mm","NF18P"]
[null,null,null,"NF28P","590 x 1290",null,null,120,112,105,null,96,590,1290,280,"Wandgehäuse schutzisoliert 590x1290x280mm IP55","NF28P"]
[null,null,null,"NF38P","840 x 1290",null,null,159,152,145,null,131,840,1290,280,"Wandgehäuse schutzisoliert 840x1290x280mm IP55","NF38P"]
[null,null,null,"NF48P","1090 x 1290",null,null,199,192,186,null,167,1090,1290,280,"Wandgehäuse schutzisoliert 1090x1290x280mm IP55","NF48P"]
[null,null,null,"NF58P","1340 x 1290",null,null,239,232,227,null,203,1340,1290,280,"Wandgehäuse schutzisoliert 1340x1290x280mm IP55","NF58P"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,280]
[null,"ABN","IP55","NF19P","340 x 1440",280,null,91,82,74,null,70,340,1440,280,"Wandgehäuse schutzisoliert IP55 BxHxT: 340x1440x280mm","NF19P"]
[null,null,null,"NF29P","590 x 1440",null,null,130,121,114,null,103,590,1440,280,"Wandgehäuse schutzisoliert 590x1440x280mm IP55","NF29P"]
[null,null,null,"NF39P","840 x 1440",null,null,172,164,157,null,140,840,1440,280,"Wandgehäuse schutzisoliert 840x1440x280mm IP55","NF39P"]
[null,null,null,"NF49P","1090 x 1440",null,null,216,208,201,null,179,1090,1440,280,"Wandgehäuse schutzisoliert 1090x1440x280mm IP55","NF49P"]
[null,null,null,"NF59P","1340 x 1440",null,null,259,252,246,null,218,1340,1440,280,"Wandgehäuse schutzisoliert 1340x1440x280mm IP55","NF59P"]
["Wandgehäuse Baureihe NT..E, SK I","ABN","IP55","NT14E","340 x 690",340,630,51,46,41,null,null,340,690,340,"Wandgehäuse geerdet 340x690x340mm IP55","NT14E"]
[null,null,null,"NT24E","590 x 690",null,null,87,68,63,null,null,590,690,340,"Wandgehäuse geerdet 590x690x340mm IP55","NT24E"]
[null,null,null,"NT34E","840 x 690",null,null,114,109,104,null,null,840,690,340,"Wandgehäuse geerdet 840x690x340mm IP55","NT34E"]
[null,null,null,"NT44E","1090 x 690",null,null,141,136,132,null,null,1090,690,340,"Wandgehäuse geerdet 1090x690x340mm IP55","NT44E"]
[null,null,null,"NT54E","1340 x 690",null,null,167,163,159,null,null,1340,690,340,"Wandgehäuse geerdet 1340x690x340mm IP55","NT54E"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,340]
[null,"ABN","IP55","NT15E","340 x 840",340,null,59,54,48,null,null,340,840,340,"Wandgehäuse geerdet 340x840x340mm IP55","NT15E"]
[null,null,null,"NT25E","590 x 840",null,null,99,93,87,null,null,590,840,340,"Wandgehäuse geerdet 590x840x340mm IP55","NT25E"]
[null,null,null,"NT35E","840 x 840",null,null,130,124,119,null,null,840,840,340,"Wandgehäuse geerdet 840x840x340mm IP55","NT35E"]
[null,null,null,"NT45E","1090 x 840",null,null,161,155,150,null,null,1090,840,340,"Wandgehäuse geerdet 1090x840x340mm IP55","NT45E"]
[null,null,null,"NT55E","1340 x 840",null,null,191,186,181,null,null,1340,840,340,"Wandgehäuse geerdet 1340x840x340mm IP55","NT55E"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,340]
[null,"ABN","IP55","NT16E","340 x 990",340,null,67,61,54,null,null,340,990,340,"Wandgehäuse geerdet 340x990x340mm IP55","NT16E"]
[null,null,null,"NT26E","590 x 990",null,null,111,104,97,null,null,590,990,340,"Wandgehäuse geerdet 590x990x340mm IP55","NT26E"]
[null,null,null,"NT36E","840 x 990",null,null,146,139,132,null,null,840,990,340,"Wandgehäuse geerdet 840x990x340mm IP55","NT36E"]
[null,null,null,"NT46E","1090 x 990",null,null,181,173,168,null,null,1090,990,340,"Wandgehäuse geerdet 1090x990x340mm IP55","NT46E"]
[null,null,null,"NT56E","1340 x 990",null,null,215,208,203,null,null,1340,990,340,"Wandgehäuse geerdet 1340x990x340mm IP55","NT56E"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,340]
[null,"ABN","IP55","NT17E","340 x 1140",340,null,85,68,60,null,null,340,1140,340,"Wandgehäuse geerdet 340x1140x340mm IP55","NT17E"]
[null,null,null,"NT27E","590 x 1140",null,null,123,114,106,null,null,590,1140,340,"Wandgehäuse geerdet 590x1140x340mm IP55","NT27E"]
[null,null,null,"NT37E","840 x 1140",null,null,161,153,146,null,null,840,1140,340,"Wandgehäuse geerdet 840x1140x340mm IP55","NT37E"]
[null,null,null,"NT47E","1090 x 1140",null,null,200,191,185,null,null,1090,1140,340,"Wandgehäuse geerdet 1090x1140x340mm IP55","NT47E"]
[null,null,null,"NT57E","1340 x 1140",null,null,238,230,224,null,null,1340,1140,340,"Wandgehäuse geerdet 1340x1140x340mm IP55","NT57E"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,340]
[null,"ABN","IP55","NT18E","340 x 1290",340,null,93,83,67,null,null,340,1290,340,"Wandgehäuse geerdet 340x1290x340mm IP55","NT18E"]
[null,null,null,"NT28E","590 x 1290",null,null,134,125,116,null,null,590,1290,340,"Wandgehäuse geerdet 590x1290x340mm IP55","NT28E"]
[null,null,null,"NT38E","840 x 1290",null,null,176,167,158,null,null,840,1290,340,"Wandgehäuse geerdet 840x1290x340mm IP55","NT38E"]
[null,null,null,"NT48E","1090 x 1290",null,null,218,209,201,null,null,1090,1290,340,"Wandgehäuse geerdet 1090x1290x340mm IP55","NT48E"]
[null,null,null,"NT58E","1340 x 1290",null,null,260,251,244,null,null,1340,1290,340,"Wandgehäuse geerdet 1340x1290x340mm IP55","NT58E"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,340]
[null,"ABN","IP55","NT19E","340 x 1440",340,null,102,91,81,null,null,340,1440,340,"Wandgehäuse geerdet 340x1440x340mm IP55","NT19E"]
[null,null,null,"NT29E","590 x 1440",null,null,145,135,125,null,null,590,1440,340,"Wandgehäuse geerdet 590x1440x340mm IP55","NT29E"]
[null,null,null,"NT39E","840 x 1440",null,null,190,180,171,null,null,840,1440,340,"Wandgehäuse geerdet 840x1440x340mm IP55","NT39E"]
[null,null,null,"NT49E","1090 x 1440",null,null,236,226,217,null,null,1090,1440,340,"Wandgehäuse geerdet 1090x1440x340mm IP55","NT49E"]
[null,null,null,"NT59E","1340 x 1440",null,null,282,272,264,null,null,1340,1440,340,"Wandgehäuse geerdet 1340x1440x340mm IP55","NT59E"]
["Wandgehäuse Baureihe NP..E, SK II","ABN","IP55","NT14P","340 x 690",340,630,51,46,41,null,null,340,690,340,"Wandgehäuse schutzisoliert 340x690x340mm IP55","NT14P"]
[null,null,null,"NT24P","590 x 690",null,null,87,68,63,null,null,590,690,340,"Wandgehäuse schutzisoliert 590x690x340mm IP55","NT24P"]
[null,null,null,"NT34P","840 x 690",null,null,114,109,104,null,null,840,690,340,"Wandgehäuse schutzisoliert 840x690x340mm IP55","NT34P"]
[null,null,null,"NT44P","1090 x 690",null,null,141,136,132,null,null,1090,690,340,"Wandgehäuse schutzisoliert 1090x690x340mm IP55","NT44P"]
[null,null,null,"NT54P","1340 x 690",null,null,167,163,159,null,null,1340,690,340,"Wandgehäuse schutzisoliert 1340x690x340mm IP55","NT54P"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,340]
[null,"ABN","IP55","NT15P","340 x 840",340,null,59,54,48,null,null,340,840,340,"Wandgehäuse schutzisoliert 340x840x340mm IP55","NT15P"]
[null,null,null,"NT25P","590 x 840",null,null,99,93,87,null,null,590,840,340,"Wandgehäuse schutzisoliert 590x840x340mm IP55","NT25P"]
[null,null,null,"NT35P","840 x 840",null,null,130,124,119,null,null,840,840,340,"Wandgehäuse schutzisoliert 840x840x340mm IP55","NT35P"]
[null,null,null,"NT45P","1090 x 840",null,null,161,155,150,null,null,1090,840,340,"Wandgehäuse schutzisoliert 1090x840x340mm IP55","NT45P"]
[null,null,null,"NT55P","1340 x 840",null,null,191,186,181,null,null,1340,840,340,"Wandgehäuse schutzisoliert 1340x840x340mm IP55","NT55P"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,340]
[null,"ABN","IP55","NT16P","340 x 990",340,null,67,61,54,null,null,340,990,340,"Wandgehäuse schutzisoliert 340x990x340mm IP55","NT16P"]
[null,null,null,"NT26P","590 x 990",null,null,111,104,97,null,null,590,990,340,"Wandgehäuse schutzisoliert 590x990x340mm IP55","NT26P"]
[null,null,null,"NT36P","840 x 990",null,null,146,139,132,null,null,840,990,340,"Wandgehäuse schutzisoliert 840x990x340mm IP55","NT36P"]
[null,null,null,"NT46P","1090 x 990",null,null,181,173,168,null,null,1090,990,340,"Wandgehäuse schutzisoliert 1090x990x340mm IP55","NT46P"]
[null,null,null,"NT56P","1340 x 990",null,null,215,208,203,null,null,1340,990,340,"Wandgehäuse schutzisoliert 1340x990x340mm IP55","NT56P"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,340]
[null,"ABN","IP55","NT17P","340 x 1140",340,null,85,68,60,null,null,340,1140,340,"Wandgehäuse schutzisoliert 340x1140x340mm IP55","NT17P"]
[null,null,null,"NT27P","590 x 1140",null,null,123,114,106,null,null,590,1140,340,"Wandgehäuse schutzisoliert 590x1140x340mm IP55","NT27P"]
[null,null,null,"NT37P","840 x 1140",null,null,161,153,146,null,null,840,1140,340,"Wandgehäuse schutzisoliert 840x1140x340mm IP55","NT37P"]
[null,null,null,"NT47P","1090 x 1140",null,null,200,191,185,null,null,1090,1140,340,"Wandgehäuse schutzisoliert 1090x1140x340mm IP55","NT47P"]
[null,null,null,"NT57P","1340 x 1140",null,null,238,230,224,null,null,1340,1140,340,"Wandgehäuse schutzisoliert 1340x1140x340mm IP55","NT57P"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,340]
[null,"ABN","IP55","NT18P","340 x 1290",340,null,93,83,67,null,null,340,1290,340,"Wandgehäuse schutzisoliert 340x1290x340mm IP55","NT18P"]
[null,null,null,"NT28P","590 x 1290",null,null,134,125,116,null,null,590,1290,340,"Wandgehäuse schutzisoliert 590x1290x340mm IP55","NT28P"]
[null,null,null,"NT38P","840 x 1290",null,null,176,167,158,null,null,840,1290,340,"Wandgehäuse schutzisoliert 840x1290x340mm IP55","NT38P"]
[null,null,null,"NT48P","1090 x 1290",null,null,218,209,201,null,null,1090,1290,340,"Wandgehäuse schutzisoliert 1090x1290x340mm IP55","NT48P"]
[null,null,null,"NT58P","1340 x 1290",null,null,260,251,244,null,null,1340,1290,340,"Wandgehäuse schutzisoliert 1340x1290x340mm IP55","NT58P"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,340]
[null,"ABN","IP55","NT19P","340 x 1440",340,null,102,91,81,null,null,340,1440,340,"Wandgehäuse schutzisoliert 340x1440x340mm IP55","NT19P"]
[null,null,null,"NT29P","590 x 1440",null,null,145,135,125,null,null,590,1440,340,"Wandgehäuse schutzisoliert 590x1440x340mm IP55","NT29P"]
[null,null,null,"NT39P","840 x 1440",null,null,190,180,171,null,null,840,1440,340,"Wandgehäuse schutzisoliert 840x1440x340mm IP55","NT39P"]
[null,null,null,"NT49P","1090 x 1440",null,null,236,226,217,null,null,1090,1440,340,"Wandgehäuse schutzisoliert 1090x1440x340mm IP55","NT49P"]
[null,null,null,"NT59P","1340 x 1440",null,null,282,272,264,null,null,1340,1440,340,"Wandgehäuse schutzisoliert 1340x1440x340mm IP55","NT59P"]
["Standgehäuse"]
["Standgehäuse Baureihe ABNRV… , SK I","ABN","IP44","ABNRV112","300 x 1980",210,630,90,80,75,null,70,300,1850,210,"Standgehäuse geerdet IP44 BxHxT: 300x1980x210mm","ABNRV112"]
[null,null,null,"ABNRV212","550 x 1980",null,null,134,126,119,null,104,550,1850,210,"Standgehäuse geerdet IP44 BxHxT: 550x1980x210mm","ABNRV212"]
[null,null,null,"ABNRV312","800 x 1980",null,null,176,169,163,null,137,800,1850,210,"Standgehäuse geerdet IP44 BxHxT: 800x1980x210mm","ABNRV312"]
[null,null,null,"ABNRV412","1050 x 1980",null,null,223,216,211,null,176,1050,1850,210,"Standgehäuse geerdet IP44 BxHxT: 1050x1980x210mm","ABNRV412"]
[null,null,null,"ABNRV512","1300 x 1980",null,null,272,265,261,null,217,1300,1850,210,"Standgehäuse geerdet IP44 BxHxT: 1300x1980x210mm","ABNRV512"]
["Standgehäuse Baureihe ABNRS… , SK II","ABN","IP44","ABNRS112","300 x 1980",210,630,90,80,75,null,70,300,1850,210,"Standgehäuse schutzisoliert IP44 BxHxT: 300x1980x210mm","ABNRS112"]
[null,null,null,"ABNRS212","550 x 1980",null,null,134,126,119,null,104,550,1850,210,"Standgehäuse schutzisoliert IP44 BxHxT: 550x1980x210mm","ABNRS212"]
[null,null,null,"ABNRS312","800 x 1980",null,null,176,169,163,null,137,800,1850,210,"Standgehäuse schutzisoliert IP44 BxHxT: 800x1980x210mm","ABNRS312"]
[null,null,null,"ABNRS412","1050 x 1980",null,null,223,216,211,null,176,1050,1850,210,"Standgehäuse schutzisoliert IP44 BxHxT: 1050x1980x210mm","ABNRS412"]
[null,null,null,"ABNRS512","1300 x 1980",null,null,272,265,261,null,217,1300,1850,210,"Standgehäuse schutzisoliert IP44 BxHxT: 1300x1980x210mm","ABNRS512"]
["Standgehäuse Baureihe SE… , SK I","ABN","IP54","SE112","300 x 1980",225,630,95,86,78,null,73,300,1850,225,"Standgehäuse geerdet 300x1980x225mm IP54","SE112"]
[null,null,null,"SE212","550 x 1980",null,null,137,129,121,null,106,550,1850,225,"Standgehäuse geerdet 550x1980x225mm IP54","SE212"]
[null,null,null,"SE312","800 x 1980",null,null,181,173,166,null,141,800,1850,225,"Standgehäuse geerdet 800x1980x225mm IP54","SE312"]
[null,null,null,"SE412","1050 x 1980",null,null,229,221,215,null,181,1050,1850,225,"Standgehäuse geerdet 1050x1980x225mm IP54","SE412"]
[null,null,null,"SE512","1300 x 1980",null,null,279,272,267,null,220,1300,1850,225,"Standgehäuse geerdet 1300x1980x225mm IP54","SE512"]
["Standgehäuse Baureihe SP… , SK II","ABN","IP54","SP112","300 x 1980",225,630,95,86,78,null,73,300,1850,225,"Standgehäuse schutzisoliert 300x1980x225mm IP54","SP112"]
[null,null,null,"SP212","550 x 1980",null,null,137,129,121,null,106,550,1850,225,"Standgehäuse schutzisoliert 550x1980x225mm IP54","SP212"]
[null,null,null,"SP312","800 x 1980",null,null,181,173,166,null,141,800,1850,225,"Standgehäuse schutzisoliert 800x1980x225mm IP54","SP312"]
[null,null,null,"SP412","1050 x 1980",null,null,229,221,215,null,181,1050,1850,225,"Standgehäuse schutzisoliert 1050x1980x225mm IP54","SP412"]
[null,null,null,"SP512","1300 x 1980",null,null,279,272,267,null,220,1300,1850,225,"Standgehäuse schutzisoliert 1300x1980x225mm IP54","SP512"]
["Standgehäuse Baureihe NF…E, SK I","ABN","IP55","NF112E","340 x 1890",280,800,116,105,94,null,90,340,1890,280,"Standgehäuse geerdet 340x1890x280mm IP55","NF112E"]
[null,null,null,"NF212E","590 x 1890",null,null,161,150,140,null,125,590,1890,280,"Standgehäuse geerdet 590x1890x280mm IP55","NF212E"]
[null,null,null,"NF312E","840 x 1890",null,null,211,200,191,null,166,840,1890,280,"Standgehäuse geerdet 840x1890x280mm IP55","NF312E"]
[null,null,null,"NF412E","1090 x 1890",null,null,263,253,245,null,212,1090,1890,280,"Standgehäuse geerdet 1090x1890x280mm IP55","NF412E"]
[null,null,null,"NF512E","1340 x 1890",null,null,317,307,300,null,259,1340,1890,280,"Standgehäuse geerdet 1340x1890x280mm IP55","NF512E"]
["Standgehäuse Baureihe NF…P, SK II","ABN","IP55","NF112P","340 x 1890",280,800,116,105,94,null,90,340,1890,280,"Standgehäuse schutzisoliert 340x1890x280mm IP55","NF112P"]
[null,null,null,"NF212P","590 x 1890",null,null,161,150,140,null,125,590,1890,280,"Standgehäuse schutzisoliert 590x1890x280mm IP55","NF212P"]
[null,null,null,"NF312P","840 x 1890",null,null,211,200,191,null,166,840,1890,280,"Standgehäuse schutzisoliert 840x1890x280mm IP55","NF312P"]
[null,null,null,"NF412P","1090 x 1890",null,null,263,253,245,null,212,1090,1890,280,"Standgehäuse schutzisoliert 1090x1890x280mm IP55","NF412P"]
[null,null,null,"NF512P","1340 x 1890",null,null,317,307,300,null,259,1340,1890,280,"Standgehäuse schutzisoliert 1340x1890x280mm IP55","NF512P"]
["Standgehäuse Baureihe NT…E, SK I, \nseitlich geschlossen","ABN","IP55","NT112E","340 x 1890",340,1200,130,116,103,null,100,340,1890,340,"Standgehäuse geerdet 340x1890x340mm IP55","NT112E"]
[null,null,null,"NT212E","590 x 1890",null,null,178,164,152,null,139,590,1890,340,"Standgehäuse geerdet 590x1890x340mm IP55","NT212E"]
[null,null,null,"NT312E","840 x 1890",null,null,230,215,205,null,185,840,1890,340,"Standgehäuse geerdet 840x1890x340mm IP55","NT312E"]
[null,null,null,"NT412E","1090 x 1890",null,null,287,274,263,null,235,1090,1890,340,"Standgehäuse geerdet 1090x1890x340mm IP55","NT412E"]
[null,null,null,"NT512E","1340 x 1890",null,null,344,331,321,null,285,1340,1890,340,"Standgehäuse geerdet 1340x1890x340mm IP55","NT512E"]
["Standgehäuse Baureihe NT…P, SK II, \nseitlich geschlossen","ABN","IP55","NT112P","340 x 1890",340,1200,130,116,103,null,100,340,1890,340,"Standgehäuse schutzisoliert 340x1890x340mm IP55","NT112P"]
[null,null,null,"NT212P","590 x 1890",null,null,178,164,152,null,139,590,1890,340,"Standgehäuse schutzisoliert 590x1890x340mm IP55","NT212P"]
[null,null,null,"NT312P","840 x 1890",null,null,230,215,205,null,185,840,1890,340,"Standgehäuse schutzisoliert 840x1890x340mm IP55","NT312P"]
[null,null,null,"NT412E","1090 x 1890",null,null,287,274,263,null,235,1090,1890,340,"Standgehäuse geerdet 1090x1890x340mm IP55","NT412E"]
[null,null,null,"NT512P","1340 x 1890",null,null,344,331,321,null,285,1340,1890,340,"Standgehäuse schutzisoliert 1340x1890x340mm IP55","NT512P"]
["Standgehäuse Baureihe NT…EB, SK I, \nseitlich offen","ABN","IP55","NT112EB","340 x 1890",340,1200,130,116,103,null,100,340,1890,340,"Standgehäuse geerdet 340x1890x340mm IP55 beideseitig offen","NT112EB"]
[null,null,null,"NT212EB","590 x 1890",null,null,178,164,152,null,139,590,1890,340,"Standgehäuse geerdet 590x1890x340mm IP55 beideseitig offen","NT212EB"]
[null,null,null,"NT312EB","840 x 1890",null,null,230,215,205,null,185,840,1890,340,"Standgehäuse geerdet 840x1890x340mm IP55 beideseitig offen","NT312EB"]
[null,null,null,"NT412EB","1090 x 1890",null,null,287,274,263,null,235,1090,1890,340,"Standgehäuse geerdet 1090x1890x340mm IP55 beideseitig offen","NT412EB"]
[null,null,null,"NT512EB","1340 x 1890",null,null,344,331,321,null,285,1340,1890,340,"Standgehäuse geerdet 1340x1890x340mm IP55 beideseitig offen","NT512EB"]
["Standgehäuse Baureihe NT…PB, SK II, \nseitlich offen","ABN","IP55","NT112PB","340 x 1890",340,1200,130,116,103,null,100,340,1890,340,"Standgehäuse schutzisoliert 340x1890x340mm IP55 beideseitig offen","NT112PB"]
[null,null,null,"NT212PB","590 x 1890",null,null,178,164,152,null,139,590,1890,340,"Standgehäuse schutzisoliert 590x1890x340mm IP55 beideseitig offen","NT212PB"]
[null,null,null,"NT312PB","840 x 1890",null,null,230,215,205,null,185,840,1890,340,"Standgehäuse schutzisoliert 840x1890x340mm IP55 beideseitig offen","NT312PB"]
[null,null,null,"NT412PB","1090 x 1890",null,null,287,274,263,null,235,1090,1890,340,"Standgehäuse schutzisoliert 1090x1890x340mm IP55 beideseitig offen","NT412PB"]
[null,null,null,"NT512PB","1340 x 1890",null,null,344,331,321,null,285,1340,1890,340,"Standgehäuse schutzisoliert 1340x1890x340mm IP55 beideseitig offen","NT512PB"]
["Standgehäuse Baureihe NS…EB, SK I, \nseitlich offen","ABN","IP55","NS212EB","590 x 1890",500,1600,226,206,186,null,182,590,1890,500,"Standgehäuse geerdet 590x1890x500mm IP55 offen","NS212EB"]
[null,null,null,"NS312EB","840 x 1890",null,null,288,267,248,null,238,840,1890,500,"Standgehäuse geerdet 840x1890x500mm IP55 offen","NS312EB"]
[null,null,null,"NS412EB","1090 x 1890",null,null,350,329,311,null,294,1090,1890,500,"Standgehäuse geerdet 1090x1890x500mm IP55 offen","NS412EB"]
[null,null,null,"NS512EB","1340 x 1890",null,null,412,391,374,null,351,1340,1890,500,"Standgehäuse geerdet 1340x1890x500mm IP55 offen","NS512EB"]
["Standgehäuse Baureihe NS…PB, SK II, \nseitlich offen","ABN","IP55","NS212PB","590 x 1890",500,1600,226,206,186,null,182,590,1890,500,"Standgehäuse schutzisoliert 590x1890x500mm IP55 offen","NS212PB"]
[null,null,null,"NS312PB","840 x 1890",null,null,288,267,248,null,238,840,1890,500,"Standgehäuse schutzisoliert 840x1890x500mm IP55 offen","NS312PB"]
[null,null,null,"NS412PB","1090 x 1890",null,null,350,329,311,null,294,1090,1890,500,"Standgehäuse schutzisoliert 1090x1890x500mm IP55 offen","NS412PB"]
[null,null,null,"NS512PB","1340 x 1890",null,null,412,391,374,null,351,1340,1890,500,"Standgehäuse schutzisoliert 1340x1890x500mm IP55 offen","NS512PB"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL175"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL175P"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL175VT"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL205"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL205P"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL205VT"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL207"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL207P"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL207VT"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL100"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL100P"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL100VT"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL101"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL101P"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL101VT"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL102"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL102P"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL102VT"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL103"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL103P"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL103VT"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL130"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL130P"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL130VT"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL131"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL131P"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL131VT"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL132"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL132P"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SL132VT"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"ABNFG133L00"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"ABNFG133M20"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"ABNFG133L06"]

{"sheet":"Tabelle 2 - Pab_Outdoor-Gehäuse","index":1,"n_rows":49,"n_cols":13,"rows_kept":49,"cut":false,"hidden":false,"merged":[[0,11,2,11],[4,0,4,6],[5,6,7,6],[9,6,11,6],[13,0,15,0],[13,1,15,1],[13,2,15,2],[9,0,11,0],[9,1,11,1],[9,2,11,2],[5,0,7,0],[5,1,7,1],[5,2,7,2],[13,6,15,6],[0,8,1,10],[0,7,1,7],[17,0,17,6],[18,0,20,0],[18,1,20,1],[18,2,20,2],[18,6,20,6],[22,0,24,0],[22,1,24,1],[22,2,24,2],[22,6,24,6],[26,0,28,0],[26,1,28,1],[26,2,28,2],[26,6,28,6],[30,6,32,6],[34,0,36,0],[34,1,36,1],[34,2,36,2],[34,6,36,6],[30,0,32,0],[30,1,32,1],[30,2,32,2],[46,0,48,0],[46,1,48,1],[46,2,48,2],[46,6,48,6],[38,0,40,0],[38,1,40,1],[38,2,40,2],[38,6,40,6],[42,0,44,0],[42,1,44,1],[42,2,44,2],[42,6,44,6]]}
["Tabelle Gehäuse-System: Angaben zur Wärmeberechnung gemäß DIN EN 61439-1, -2, -3",null,null,null,null,null,null,"Abstrahlbare Verlustleistung","BxHxT für Wärmeberechung (ohne Sockel)\n[mm]",null,null,"Beschreibung"]
[]
["Schrankart","Hersteller","Schutzart","Typ","Ausführung","B x H\n[mm]","Tiefe\n[mm]","Beideseitg Frei Ruckwand Frei,\n20K 75% Gehäusehöhe","B,mm","H,mm","T,mm"]
[]
["Verteilersäule"]
["Verteilersäule Baureihe SL175\nBauhöhe 5","ABN","IP44","SL175","Leergehäuse","583  x 1710",277,116,583,1060,277,"Anschlusssäule FB2 BH5 ohne Ausbau mit Sockel Doppelschließung 1 Zylinder",277]
[null,null,null,"SL175P","Leergehäuse mit Montageplatte","583  x 1710",null,116,583,1060,277,"Anschlusssäule FB2 BH5 mit Montageplatte Doppelschließung 1 Zylinder",277]
[null,null,null,"SL175VT","Systemgehäuse mit Ausbausystem Prisma XS","583  x 1710",null,62,540,751,140,"Anschlusssäule FB2 BH5 Prisma XS-Volltür Doppelschließung 1 Zylinder",277]
[null,null,null,null,null,null,null,null,null,null,null,null,277]
["Verteilersäule Baureihe SL20. \nBauhöhe 7","ABN","IP44","SL205","Leergehäuse","583 x 2010",277,139,583,1360,277,"Anschlusssäule FB2 BH7 ohne Ausbau mit Sockel Doppelschließung 1 Zylinder",277]
[null,null,null,"SL205P","Leergehäuse mit Montageplatte","583 x 2010",null,139,583,1360,277,"Anschlusssäule FB2 BH7 mit Montageplatte Doppelschließung 1 Zylinder",277]
[null,null,null,"SL205VT","Systemgehäuse mit Ausbausystem Prisma XS","583 x 2010",null,81,540,1051,140,"Anschlusssäule FB2 BH7 Prisma XS-Volltür Doppelschließung 1 Zylinder",277]
[null,null,null,null,null,null,null,null,null,null,null,null,277]
["Verteilersäule Baureihe SL20. \nBauhöhe 7","ABN","IP44","SL207","Leergehäuse","838 x 2010",277,183,838,1300,277,"Anschlusssäule FB3 BH7 1 Zylinder eingebaut Doppelschließung",277]
[null,null,null,"SL207P","Leergehäuse mit Montageplatte","838 x 2010",null,183,838,1300,277,"Anschlusssäule FB3 BH7 mit Montageplatte 1 Zylinder eingebaut",277]
[null,null,null,"SL207VT","Systemgehäuse mit Ausbausystem Prisma XS","838 x 2010",null,109,747,1051,140,"Anschlusssäule FB3 BH7 Prisma XS-Volltür H:2010mm",277]
[]
["Anschlussschränke"]
["Anschlussschrank Baureihe SL100 \nBauhöhe 6","ABN","IP44","SL100","Leergehäuse","585 x 1005",315,120,null,null,null,"Kabelverteilerschrank FB2 BH6 ohne Ausbau Gr.0/1005mm Doppelschließung 1 Zylinder",315]
[null,null,null,"SL100P","Leergehäuse mit Montageplatte","585 x 1005",null,120,null,null,null,"Kabelverteilerschrank FB2 BH6 mit Montageplatte Gr.0/1005mm Doppelschließung 1 Zylinder",315]
[null,null,null,"SL100VT","Systemgehäuse mit Ausbausystem Prisma XS","585 x 1005",null,68,514,901,140,"Kabelverteilerschrank FB2 BH6 Prisma XS-Volltür Gr.0/1005mm Doppelschließung 1 Zylinder",315]
[null,null,null,null,null,null,null,null,null,null,null,null,315]
["Anschlussschrank Baureihe SL101\nBauhöhe 6","ABN","IP44","SL101","Leergehäuse","780 x 1005",315,151,null,"-",null,"Kabelverteilerschrank FB3 BH6 ohne Ausbau Gr.1/1005mm Doppelschließung 1 Zylinder",315]
[null,null,null,"SL101P","Leergehäuse mit Montageplatte","780 x 1005",null,151,null,"-",null,"Kabelverteilerschrank FB3 BH6 mit Montageplatte Gr.1/1005mm Doppelschließung 1 Zylinder",315]
[null,null,null,"SL101VT","Systemgehäuse mit Ausbausystem Prisma XS","780 x 1005",null,97,750,901,140,"Kabelverteilerschrank FB3 BH6 Prisma XS-Volltür Gr.1/1005mm Doppelschließung 1 Zylinder",315]
[null,null,null,null,null,null,null,null,null,null,null,null,315]
["Anschlussschrank Baureihe SL102\nBauhöhe 6","ABN","IP44","SL102","Leergehäuse","1110 x 1005",315,205,null,"-",null,"Kabelverteilerschrank FB4 BH6 ohne Ausbau Gr.2/1005mm Doppelschließung 1 Zylinder",315]
[null,null,null,"SL102P","Leergehäuse mit Montageplatte","1110 x 1005",null,205,null,"-",null,"Kabelverteilerschrank FB4 BH6 mit Montageplatte Gr.2/1005mm Doppelschließung 1 Zylinder",315]
[null,null,null,"SL102VT","Systemgehäuse mit Ausbausystem Prisma XS","1110 x 1005",null,133,1039,901,140,"Kabelverteilerschrank FB4 BH6 Prisma XS-Volltür Gr.2/1005mm Doppelschließung 1 Zylinder",315]
[null,null,null,null,null,null,null,null,null,null,null,null,315]
["Anschlussschrank Baureihe SL103 \nBauhöhe 6","ABN","IP44","SL103","Leergehäuse","1445 x 1080",315,273,null,"-",null,"Kabelverteilerschrank FB5 BH8 ohne Ausbau Gr.3/1065mm Doppelschließung 1 Zylinder",315]
[null,null,null,"SL103P","Leergehäuse mit Montageplatte","1445 x 1080",null,273,null,"-",null,"Kabelverteilerschrank FB5 BH8  mit Montageplatte Gr.3/1065mm Doppelschließung 1 Zylinder",315]
[null,null,null,"SL103VT","Systemgehäuse mit Ausbausystem Prisma XS","1445 x 1080",null,175,1369,901,140,"Kabelverteilerschrank FB5 BH8 Prisma XS-Volltür Gr.3/1065mm Doppelschließung 1 Zylinder",315]
[null,null,null,null,null,null,null,null,null,null,null,null,315]
["Anschlussschrank Baureihe SL130\nBauhöhe 8","ABN","IP44","SL130","Leergehäuse","585 x 1335",315,147,null,"-",null,"Kabelverteilerschrank FB2 BH8 ohne Ausbau Gr.0/1355mm Doppelschließung 1 Zylinder",315]
[null,null,null,"SL130P","Leergehäuse mit Montageplatte","585 x 1335",null,147,null,"-",null,"Kabelverteilerschrank FB2 BH8 mit Montageplatte Gr.0/1355mm Doppelschließung 1 Zylinder",315]
[null,null,null,"SL130VT","Systemgehäuse mit Ausbausystem Prisma XS","585 x 1335",null,88,514,1201,140,"Kabelverteilerschrank FB2 BH8 Prisma XS-Volltür Gr.0/1355mm Doppelschließung 1 Zylinder",315]
[null,null,null,null,null,null,null,null,null,null,null,null,315]
["Anschlussschrank Baureihe SL131 \nBauhöhe 8","ABN","IP44","SL131","Leergehäuse","780 x 1335",315,186,null,"-",null,"Kabelverteilerschrank FB3 BH8 ohne Ausbau Gr.1/1355mm Doppelschließung 1 Zylinder",315]
[null,null,null,"SL131P","Leergehäuse mit Montageplatte","780 x 1335",null,186,null,"-",null,"Kabelverteilerschrank FB3 BH8 mit Montageplatte Gr.1/1355mm Doppelschließung 1 Zylinder",315]
[null,null,null,"SL131VT","Systemgehäuse mit Ausbausystem Prisma XS","780 x 1335",null,121,750,1201,140,"Kabelverteilerschrank FB3 BH8 Prisma XS-Volltür Gr.1/1355mm Doppelschließung 1 Zylinder",315]
[null,null,null,null,null,null,null,null,null,null,null,null,315]
["Anschlussschrank Baureihe SL132 \nBauhöhe 8","ABN","IP44","SL132","Leergehäuse","1110 x 1335",315,253,null,"-",null,"Kabelverteilerschrank FB4 BH8 ohne Ausbau Gr.2/1355mm Doppelschließung 1 Zylinder",315]
[null,null,null,"SL132P","Leergehäuse mit Montageplatte","1110 x 1335",null,253,null,"-",null,"Kabelverteilerschrank FB4 BH8 mit Montageplatte Gr.2/1355mm Doppelschließung 1 Zylinder",315]
[null,null,null,"SL132VT","Systemgehäuse mit Ausbausystem Prisma XS","1110 x 1335",null,165,1039,1201,140,"Kabelverteilerschrank FB4 BH8 Prisma XS-Volltür Gr.2/1355mm Doppelschließung 1 Zylinder",315]
[null,null,null,null,null,null,null,null,null,null,null,null,315]
["Anschlussschrank Baureihe SL133\nBauhöhe 8","ABN","IP44","ABNFG133L00","Leergehäuse","1445 x 1350",315,326,null,"-",null,"Kabelverteilerschrank FB5 BH8 ohne Ausbau Gr.3/1350mm Doppelschließung 1 Zylinder",315]
[null,null,null,"ABNFG133M20","Leergehäuse mit Montageplatte","1445 x 1350",null,326,null,"-",null,"Kabelverteilerschrank FB5 BH8 mit Montageplatte Gr.3/1350mm Doppelschließung 1 Zylinder",315]
[null,null,null,"ABNFG133L06","Systemgehäuse mit Ausbausystem Prisma XS","1445 x 1350",null,224,1369,1245,140,"Kabelverteilerschrank FB5 BH8 Prisma XS-Volltür Gr.3/1350mm Doppelschließung 1 Zylinder",315]

{"sheet":"Tabelle 3 - Pv_Einbaugeräte","index":2,"n_rows":2300,"n_cols":11,"rows_kept":2300,"cut":false,"hidden":false,"merged":[[11,3,13,3],[28,3,30,3],[111,3,114,3],[357,3,358,3],[117,3,119,3],[58,3,62,3],[64,1,71,1],[73,1,79,1],[80,1,84,1],[136,1,137,1],[33,3,34,3],[54,3,55,3],[39,3,47,3],[48,3,53,3],[6,3,9,3],[359,3,362,3],[365,3,367,3],[368,3,370,3],[123,3,124,3],[355,3,356,3],[126,3,128,3],[4,3,5,3],[109,3,110,3],[26,3,27,3],[102,3,108,3],[37,3,38,3],[91,3,94,3],[98,3,99,3],[100,3,101,3],[14,3,17,3],[20,3,22,3],[18,3,19,3],[23,3,25,3],[31,3,32,3],[422,1,424,1],[219,1,220,1],[223,1,224,1],[379,1,387,1],[388,1,394,1],[395,1,402,1],[403,1,410,1],[415,1,418,1],[411,1,414,1],[247,1,250,1],[354,1,362,1],[227,1,232,1],[234,1,239,1],[240,1,243,1],[244,1,246,1],[363,1,370,1],[4,1,10,1],[87,1,88,1],[89,1,96,1],[133,1,134,1],[56,1,63,1],[28,1,35,1],[11,1,27,1],[102,1,116,1],[117,1,122,1],[100,1,101,1],[97,1,99,1],[36,1,55,1],[123,1,128,1],[411,3,413,3],[415,3,416,3],[392,3,394,3],[395,3,396,3],[398,3,399,3],[400,3,402,3],[403,3,404,3],[406,3,407,3],[408,3,410,3],[408,5,410,5],[373,3,374,3],[371,1,378,1],[375,3,378,3],[380,3,381,3],[384,3,387,3],[388,3,389,3],[382,3,383,3]]}
[null,"Tabelle Einbaugeräte:"]
[]
["Gruppe","Geräteart","Typ / \nBestellnummer","Bemerkung","Hersteller","Bemessungs\nstrom des Gerätes\nIn [A]","Verlustleistung Pro Pol  bei Bemessungsstrom\nin Watt","Verlustleistung des Gerätes  bei Bemessungsstrom\nin Watt","Verlustleistung der Sicherung (pro Pol) bei Bemessungsstrom","Verlustleistung  Bemessungsstrom (pro Pol)\nPV / W\n\nSumme Spalte G + H","Beschreibung"]
[null,"Sicherungslasttrennschalter "]
["Sicherungslasttrennschalter","Sicherungslasttrennschalter NH 000, einschl. Sicherung","E-XTR506EU","NH-Trenner SaS 40mm, 3 Pol","ABN","100",{"$f":"H5/3","v":4.333333333333333},13,6.6,{"$f":"G5+I5","v":10.933333333333334},"NH000-SLT 690V AC, 3-polig  für SAS 40/12mm Abgang unten, Rahmenklemme 2,5-50mm²"]
["Sicherungslasttrennschalter",null,"E-XTR506EO",null,"ABN",100,{"$f":"H6/3","v":4.333333333333333},13,6.6,{"$f":"G6+I6","v":10.933333333333334},"NH000-SLT 690V AC, 3-polig  für SAS 40/12mm Abgang oben, Rahmenklemme 2,5-50mm²"]
["Sicherungslasttrennschalter",null,"XTR606","NH-Trenner SaS 60mm, 3 Pol","ABN",100,{"$f":"H7/3","v":3.6666666666666665},11,6.6,{"$f":"G7+I7","v":10.266666666666666},"NH Trenner Gr.000 Abgang oben SaS 60mm EBM 32/70mm"]
["Sicherungslasttrennschalter",null,"XTR606U",null,"ABN",100,{"$f":"H8/3","v":3.6666666666666665},11,6.6,{"$f":"G8+I8","v":10.266666666666666},"NH Trenner Gr.000 Abgang unten SaS 60mm EBM 32/70mm"]
["Sicherungslasttrennschalter",null,"LV480751",null,"ABN",100,3.6666666666666665,11,6.6,10.266666666666666,"Sicherungslasttrennschalter ISFT100N 3P Anschluss 60 mm Sammelschiene"]
["Sicherungslasttrennschalter",null,"LV480752",null,"ABN",100,3.6666666666666665,11,6.6,10.266666666666666,"Sicherungslasttrennschalter ISFT100N 3P Anschluss 60 mm Sammelschiene"]
["Sicherungslasttrennschalter",null,"LV480750","NH-Trenner MPL, 3 Pol","ABN",100,{"$f":"H11/3","v":3.6666666666666665},11,6.6,{"$f":"G11+I11","v":10.266666666666666},"Sicherungslasttrennschalter ISFT100N 3p Anschluss 2,5 bis 50qmm Montageplatte"]
["Sicherungslasttrennschalter","Sicherungslasttrennschalter NH 00, einschl. Sicherung","E-XTR209","NH-Trenner SaS 40mm, 3Pol","ABN",160,{"$f":"H12/3","v":4},12,11.2,{"$f":"G12+I12","v":15.2},"NH-Trenner Gr.00 DTL160FTSW/BK Montage a.Ssch. 40mm"]
["Sicherungslasttrennschalter",null,"XTR209",null,"ABN",160,{"$f":"H13/3","v":4},12,11.2,{"$f":"G13+I13","v":15.2},"NH-Trenner Gr.00 mit Brückenklemme_SaS40 Montage auf Sammelschienen 40mm"]
["Sicherungslasttrennschalter",null,"XTR509",null,"ABN",160,{"$f":"H14/3","v":6.333333333333333},19,11.2,{"$f":"G14+I14","v":17.533333333333331},"NH Trenner Gr.00 Universal-Anschluß SaS 40mm EBM 70mm"]
["Sicherungslasttrennschalter",null,"XTR609","NH-Trenner SaS 60mm, 3Pol","ABN",160,5.666666666666667,17,11.2,16.866666666666667,"NH Trenner Gr.00 Universal-Anschluß SaS 60mm EBM 70mm"]
["Sicherungslasttrennschalter",null,"XTR609K",null,"ABN",160,{"$f":"H16/3","v":5.666666666666667},17,11.2,{"$f":"G16+I16","v":16.866666666666667},"NH Trenner Gr.00 Kastenklemme SaS 60mm EBM 32/70mm"]
["Sicherungslasttrennschalter",null,"LV480803",null,"ABN",160,{"$f":"H17/3","v":5.666666666666667},17,11.2,{"$f":"G17+I17","v":16.866666666666667},"Sicherungslasttrennschalter ISFT160 3P  Anschluss 60 mm Sammelschiene"]
["Sicherungslasttrennschalter",null,"XTR408",null,"ABN",160,5.9,null,11.2,{"$f":"G18+I18","v":17.100000000000001},"NH-Trenner Gr.00 mit Brückenklemme Montage auf Sammelschienen 60mm (Wöhner)"]
["Sicherungslasttrennschalter",null,"XTL703","NH-LS-Leiste SaS 60mm, 3Pol","ABN",160,{"$f":"H19/3","v":6.666666666666667},20,11.2,{"$f":"G19+I19","v":17.866666666666667},"NH-Trennerleiste Gr.00 Universal-Anschluß EBM 70mm auf SaS 60mm"]
["Sicherungslasttrennschalter",null,"LV480850",null,"ABN",160,{"$f":"H20/3","v":6.666666666666667},20,11.2,{"$f":"G20+I20","v":17.866666666666667},"Sicherungslasttrennschalter ISFL160 3P Anschluss 60 mm Sammelschiene M8"]
["Sicherungslasttrennschalter",null,"EH041AAC","NH-LS-Leiste SaS 185mm, 3Pol","ABN",160,7.333333333333333,22,11.2,18.533333333333331,"NH-Sicherungslastschalter-Leiste Gr.00 690V/160A Schraubanschluss M8x20mm 1p Schaltbar"]
["Sicherungslasttrennschalter",null,"EH041CAD",null,"ABN",160,{"$f":"H22/3","v":7.333333333333333},22,11.2,{"$f":"G22+I22","v":18.533333333333331},"NH-Sicherungslastschaltleiste Gr.00 V-Klemme 95 mm² se 1p schaltbar 690V/160A"]
["Sicherungslasttrennschalter",null,"EH052CAD",null,"ABN",160,7.333333333333333,22,11.2,18.533333333333331,"NH-Sicherungsleiste Größe 00 Stahlrahmen V-Klemme 10-95 mm² 690V/160A"]
["Sicherungslasttrennschalter",null,"XTL903W","NH-LS-Leiste SaS 185mm, 3Pol","ABN",160,{"$f":"H24/3","v":7.333333333333333},22,11.2,{"$f":"G24+I24","v":18.533333333333331},"NH-Trennerleiste Gr.00 für Wandler EBM 150mm auf SaS 185mm"]
["Sicherungslasttrennschalter",null,"XTL904",null,"ABN",160,{"$f":"H25/3","v":7.333333333333333},22,11.2,18.533333333333331,"NH-Trennerleiste Gr.00 EBM 125mm auf SaS 185mm Universal-Anschluß"]
["Sicherungslasttrennschalter",null,"XTL903",null,"ABN",160,{"$f":"H26/3","v":7.333333333333333},22,11.2,18.533333333333331,"NH-Trennerleiste Gr.00 EBM 150mm auf SaS 185mm Universal-Anschluß"]
["Sicherungslasttrennschalter",null,"XTR309","NH-Trenner, MPL, 3Pol","ABN",160,{"$f":"H27/3","v":4.333333333333333},13,11.2,{"$f":"G27+I27","v":15.533333333333331},"NH Trenner Gr.00 Universal-Anschluß Montage auf Montage-Traverse"]
["Sicherungslasttrennschalter",null,"LV480801",null,"ABN",160,{"$f":"H28/3","v":4.333333333333333},13,11.2,{"$f":"G28+I28","v":15.533333333333331},"Sicherungslasttrennschalter ISFT160 3P Anschluss M8 Montageplatte"]
["Sicherungslasttrennschalter","Sicherungslasttrennschalter NH 1, einschl. Sicherung","XTR512","NH-Trenner, SaS 40mm, 3Pol","ABN",250,{"$f":"H29/3","v":8.6666666666666661},26,17,{"$f":"G29+I29","v":25.666666666666664},"NH Trenner Gr.1 Universal-Anschluß SaS 40mm EBM 70mm"]
["Sicherungslasttrennschalter",null,"XTR513E",null,"ABN",250,{"$f":"H30/3","v":9},27,17,{"$f":"G30+I30","v":26},"Einspeise Trenner NH1 Schraubanschluß M10 (Jung) Für Sammelschienen 40mm, EBM 70mm Abgang oben"]
["Sicherungslasttrennschalter",null,"XTR513EU",null,"ABN",250,{"$f":"H31/3","v":9},27,17,{"$f":"G31+I31","v":26},"Einspeise Trenner NH1 Schraubanschluß M10 (Jung) Für Sammelschienen 40mm, EBM 70mm Abgang unten"]
["Sicherungslasttrennschalter",null,"XTR712","NH-Trenner, SaS 60mm, 3Pol","ABN",250,7.666666666666667,23,17,24.666666666666668,"NH Trenner Gr.1 Universal-Anschluß SaS 60mm EBM 70mm"]
["Sicherungslasttrennschalter",null,"XTR712E",null,"ABN",250,{"$f":"H33/3","v":7.666666666666667},23,17,{"$f":"G33+I33","v":24.666666666666668},"Einspeise NH-Trenner Gr.1 Montage auf Sammelschienen 60mm, EBM 70mm"]
["Sicherungslasttrennschalter",null,"LV480856","NH-LS-Leiste 185mm SaS, 3Pol","ABN",250,{"$f":"H34/3","v":9},27,17,{"$f":"G34+I34","v":26},"Sicherungslasttrennschalter ISFL250 3P Anschluss 185 mm Sammelschiene M12"]
["Sicherungslasttrennschalter",null,"XTL912W",null,"ABN",250,9,27,17,26,"NH-Trennerleiste Gr.1 für Wandler EBM 150mm auf SaS 185mm"]
["Sicherungslasttrennschalter",null,"XTR312","NH-Trenner, MPL, 3Pol","ABN",250,{"$f":"H36/3","v":7.666666666666667},23,17,{"$f":"G36+I36","v":24.666666666666668},"NH Trenner Gr.1 Universal-Anschluß Montage auf Montage-Traverse"]
["Sicherungslasttrennschalter","Sicherungslasttrennschalter NH 2, einschl. Sicherung","E-XTR522","NH-Trenner SaS 40mm, 3Pol","ABN",400,23.333333333333332,70,29,52.333333333333329,"NH-Sicherungs-Lasttrenner Gr.2 für SAS 40/12mm 3pol., 400A, Universalanschluss M10"]
["Sicherungslasttrennschalter",null,"XTR722","NH-Trenner SaS 60mm, 3Pol","ABN",400,23,69,29,52,"NH Trenner Gr.2 Universal-Anschluß SaS 60mm EBM 70mm"]
["Sicherungslasttrennschalter",null,"XTR722E",null,"ABN",400,{"$f":"H39/3","v":23},69,29,{"$f":"G39+I39","v":52},"Einspeise NH-Trenner Gr.2 Montage auf Sammelschienen 60mm, EBM 70mm"]
["Sicherungslasttrennschalter",null,"EH231CAA","NH-LS-Leiste 185mm SaS, 3Pol","ABN",400,17.333333333333332,52,29,46.333333333333329,"NH-Sich-Leiste Gr.2  690V/400A V-D-Klemmen 35-240qmm+Berührschutz"]
["Sicherungslasttrennschalter",null,"EH232CAB",null,"ABN",400,{"$f":"H41/3","v":17.333333333333332},52,29,{"$f":"G41+I41","v":46.333333333333329},"NH-Sicherungslastschaltleiste Gr.2 V-Doppelklemme 35-240 mm² Anschlussabdeckung 690V/400A"]
["Sicherungslasttrennschalter",null,"EH241AAB",null,"ABN",400,17.333333333333332,52,29,46.333333333333329,"NH-SLS-Leiste Gr.2  690V/400A EON Ausführung"]
["Sicherungslasttrennschalter",null,"EH241AAG",null,"ABN",400,17.333333333333332,52,29,46.333333333333329,"NH-Sicherungslastschaltleiste Gr.2 M12x35mm Schraubenanschluss 1p schaltbar 690V/400A"]
["Sicherungslasttrennschalter",null,"EH241CAC",null,"ABN",400,17.333333333333332,52,29,46.333333333333329,"NH-Sicherungslastschaltleiste Gr.2 V-Klemme 240 mm² se 5-Leiter 1p 690V/400A"]
["Sicherungslasttrennschalter",null,"E-EH241CAC",null,"ABN",400,{"$f":"H45/3","v":17.333333333333332},52,29,{"$f":"G45+I45","v":46.333333333333329},"NH-SLS-Leiste Gr.2  690V/400A V-D-Klemmen 35-240qmm,1-p.sb."]
["Sicherungslasttrennschalter",null,"EH241CAL",null,"ABN",400,17.333333333333332,52,29,46.333333333333329,"NH2/400A LS-Leiste o.E-Verpack Export,m. V-Klemm/300se, 1-polig schaltbar"]
["Sicherungslasttrennschalter",null,"EH243AAB",null,"ABN",400,17.333333333333332,52,29,46.333333333333329,"NH-SLS-Leiste Gr.2  690V/400A Schraubanschluss M12x30mm,3-polig, schaltbar"]
["Sicherungslasttrennschalter",null,"EH243CAA",null,"ABN",400,17.333333333333332,52,29,46.333333333333329,"NH-SLS-Leiste Gr.2  690V/400A V-D-Klemmen 50-185,3-polig schaltbar"]
["Sicherungslasttrennschalter",null,"XTL921V","NH-LS-Leiste 185mm SaS, 3Pol","ABN",400,18.666666666666668,56,29,47.666666666666671,"NH-Trennerleiste Gr.2 mit V-Anschluß 1p schaltbar für 185mm SaS mit Befestigungsschrauben"]
["Sicherungslasttrennschalter",null,"XTL921W",null,"ABN",400,18.666666666666668,56,29,47.666666666666671,"NH-Trennerleiste Gr.2 Universal-Anschluß M12 1p schaltbar für 185mm SaS mit Befestigungsschrauben"]
["Sicherungslasttrennschalter",null,"XTL922V",null,"ABN",400,{"$f":"H51/3","v":18.666666666666668},56,29,{"$f":"G51+I51","v":47.666666666666671},"NH-Trennerleiste Gr.2 mit V-Anschluss 3p schaltbar für 185mm SaS mit Befestigungsschrauben"]
["Sicherungslasttrennschalter",null,"XTL922W",null,"ABN",400,{"$f":"H52/3","v":18.666666666666668},56,29,{"$f":"G52+I52","v":47.666666666666671},"NH-Trennerleiste Gr.2 für Wandler EBM 150mm auf SaS 185mm"]
["Sicherungslasttrennschalter",null,"LV480857",null,"ABN",400,{"$f":"H53/3","v":18.666666666666668},56,29,{"$f":"G53+I53","v":47.666666666666671},"Sicherungslasttrennschalter ISFL400 3P Anschluss 185 mm Sammelschiene M12"]
["Sicherungslasttrennschalter",null,"LV480902",null,"ABN",400,18.666666666666668,56,29,47.666666666666671,"NH Trenner Leiste Gr.2 1p schaltbar Montiert auf SammelS 185mm (M12)"]
["Sicherungslasttrennschalter",null,"XTR322","NH-Trenner, MPL, 3Pol","ABN",400,{"$f":"H55/3","v":15.333333333333334},46,29,{"$f":"G55+I55","v":44.333333333333336},"NH Trenner Gr.2 Universal-Anschluß Montage auf Montage-Traverse"]
["Sicherungslasttrennschalter",null,"LV480806",null,"ABN",400,{"$f":"H56/3","v":15.333333333333334},46,29,{"$f":"G56+I56","v":44.333333333333336},"Sicherungslasttrennschalter ISFT400 3P Anschluss M10 Montageplatte"]
["Sicherungslasttrennschalter","Sicherungslasttrennschalter NH 3, einschl. Sicherung","XTR732","NH-Trenner, SaS 60mm, 3Pol","ABN",630,31,93,40.200000000000003,71.2,"NH Trenner Gr.3 Universal-Anschluß SaS 60mm EBM 70mm"]
["Sicherungslasttrennschalter",null,"XTL932K","NH-LS-Koppelleiste 185mm SaS, 3Pol","ABN",630,36.666666666666664,110,40.200000000000003,76.866666666666674,"NH-LSL NH3 als Koppelleiste 630A für System 185mm ohne Platzverlust (nur Schraubmontage!!)"]
["Sicherungslasttrennschalter",null,"EH341AAB","NH-LS-Leiste 185mm SaS, 3Pol","ABN",630,40,120,40.200000000000003,80.2,"NH-Sicherungslastschaltleiste Gr.3 630A M12x35mm Schraubenanschluss 1p schaltbar"]
["Sicherungslasttrennschalter",null,"EH343AAB",null,"ABN",630,{"$f":"H60/3","v":40},120,40.200000000000003,{"$f":"G60+I60","v":80.2},"NH-Sicherungslastschaltleiste Gr.3 630A M12x30mm Schraubenanschluss 3p schaltbar"]
["Sicherungslasttrennschalter",null,"EH343CAA",null,"ABN",630,40,120,40.200000000000003,80.2,"NH-SLS-Leiste Gr.3  630A V-Klemme 300se, 3-polig schaltbar"]
["Sicherungslasttrennschalter",null,"LV480858",null,"ABN",630,37,111,40.200000000000003,77.2,"Sicherungslasttrennschalter ISFL630 3P Anschluss 185 mm Sammelschiene M12"]
["Sicherungslasttrennschalter",null,"XTL932W",null,"ABN",630,37,111,40.200000000000003,77.2,"NH-Trennerleiste Gr.3 für Wandler EBM 150mm auf SaS 185mm"]
["Sicherungslasttrennschalter",null,"XTR332","NH-Trenner, MPL, 3Pol","ABN",630,{"$f":"H64/3","v":31},93,40.200000000000003,{"$f":"G64+I64","v":71.2},"NH Trenner Gr.3 Universal-Anschluß Montage auf Montage-Traverse"]
["Sicherungslasttrennschalter","Reiter-Sicherungs-Schalter, 10,3x38, einschl. Sicherung","XTNR363","SaS 60mm, 3 Pol","ABN","63",{"$f":"H65/3","v":3.5},10.5,5.5,{"$f":"G65+I65","v":9},"D02-Lasttrennschalter Neozed E18, 63A, 400V, 3-polig Reiter (Wöhner)"]
["Sicherungslasttrennschalter",null,"A9N15656","auf Hutschiene, 3 Pol","Schneider","25",3,9,3,{"$f":"G66+I66","v":6},"Acti 9-Sicherungstrennschalter STI, 3-polig, 25A,  für Sicherung 10,3x38mm"]
["Sicherungslasttrennschalter",null,"A9N15646","auf Hutschiene, 1 Pol+N","Schneider",25,1,null,3,{"$f":"G67+I67","v":4},"Acti 9, Sicherungstrennschalter STI, 1-polig+N,  25A, für Sicherung 10,3x38mm"]
["Sicherungslasttrennschalter",null,"A9N15651","auf Hutschiene, 2 Pol","Schneider",25,1,null,3,{"$f":"G68+I68","v":4},"Acti 9, Sicherungstrennschalter STI, 2-polig, 25A, für Sicherung 10,3x38mm"]
["Sicherungslasttrennschalter",null,"A9N15636","auf Hutschiene, 1 Pol","Schneider",25,1,null,3,{"$f":"G69+I69","v":4},"SICHERUNGSTRÄGERSTI 1P 1 3 X 38 500V"]
["Sicherungslasttrennschalter",null,"A9N15658","auf Hutschiene, 3 Pol","Schneider",25,1,null,3,4,"SICHERUNGSTRÄGERSTI 3P+N 10,3 X 38  500V"]
["Sicherungslasttrennschalter",null,"DF101","auf Hutschiene, 1 Pol","Schneider",25,1,null,3,{"$f":"G71+I71","v":4},"Sicherungshalter TeSys 1p 25A Sicherungsgröße 10x38mm"]
["Sicherungslasttrennschalter",null,"DF103","auf Hutschiene, 3 Pol","Schneider",32,1,null,3,4,"Sicherungshalter TeSys 3p 32A Sicherungsgröße 10x38mm"]
["Sicherungslasttrennschalter","Acti 9, Sicherungstrennschalter STI, 1-polig, 10A, für Sicherung 8,5x31,5mm","A9N15635","auf Hutschiene, 1 Pol","Schneider",10,1,null,2.5,3.5,"Acti 9, Sicherungstrennschalter STI, 1-polig, 10A, für Sicherung 8,5x31,5mm"]
["Sicherungslasttrennschalter","Sicherungs-Lasttrennschalter D01, einschl. Sicherung","MGN01610","auf Hutschiene, 1p+N","Schneider",10,1,null,1.5,2.5,"Sicherungs-Lasttrennschalter D01, 1p+N, 10A"]
["Sicherungslasttrennschalter",null,"MGN01710","auf Hutschiene, 3p+N","Schneider",10,1,null,1.5,2.5,"Sicherungs-Lasttrennschalter D01, 3p+N, 10A"]
["Sicherungslasttrennschalter",null,"MGN01613","auf Hutschiene, 1p+N","Schneider",13,1,null,1.8,2.8,"Sicherungs-Lasttrennschalter D01, 1p+N, 13A"]
["Sicherungslasttrennschalter",null,"MGN01713","auf Hutschiene, 3p+N","Schneider",13,1,null,1.8,2.8,"Sicherungs-Lasttrennschalter D01, 3p+N, 13A"]
["Sicherungslasttrennschalter",null,"MGN01616","auf Hutschiene, 1p+N","Schneider",16,1,null,2.2999999999999998,3.3,"Sicherungs-Lasttrennschalter D01, 1p+N, 16A"]
["Sicherungslasttrennschalter",null,"MGN01316","auf Hutschiene, 3p","Schneider",16,1,null,2.2999999999999998,3.3,"Sicherungs-Lasttrennschalter D01, 3p, 16A"]
["Sicherungslasttrennschalter",null,"MGN01716","auf Hutschiene, 3p+N","Schneider",16,1,null,2.2999999999999998,{"$f":"G80+I80","v":3.3},"Sicherungs-Lasttrennschalter D01, 3p+N, 16A"]
["Sicherungslasttrennschalter","Sicherungs-Lasttrennschalter D02, einschl. Sicherung","MGN02163","auf Hutschiene, 1p","Schneider",63,1.5,null,5.4,{"$f":"G81+I81","v":6.9},"Sicherungs-Lasttrennschalter D02, 1p, 63A"]
["Sicherungslasttrennschalter",null,"MGN02663","auf Hutschiene, 1p+N","Schneider",63,1.5,null,5.4,{"$f":"G82+I82","v":6.9},"Sicherungs-Lasttrennschalter D02, 1p+N, 63A"]
["Sicherungslasttrennschalter",null,"MGN02263","auf Hutschiene, 2p","Schneider",63,1.5,null,5.4,{"$f":"G83+I83","v":6.9},"Sicherungs-Lasttrennschalter D02, 2p, 63A"]
["Sicherungslasttrennschalter",null,"MGN02363","auf Hutschiene, 3p","Schneider",63,1.5,null,5.4,{"$f":"G84+I84","v":6.9},"Sicherungs-Lasttrennschalter D02, 3p, 63A"]
["Sicherungslasttrennschalter",null,"MGN02763","auf Hutschiene, 3p+N","Schneider",63,1.5,null,5.4,{"$f":"G85+I85","v":6.9},"Sicherungs-Lasttrennschalter D02, 3p+N, 63A"]
[]
["Sicherungsträger","Sicherungsträger"]
["Sicherungsträger","Schraubsicherungssystem D 01/E14, einschl. Sicherung","R9J01116","auf Hutschiene, 1 Pol","Schneider",16,{"$f":"H88","v":4},4,2.5,6.5,"Neozed Sicherungssockel D01, 1P, 16A, 400V, DIN-Schiene"]
["Sicherungsträger",null,"R9J01316","auf Hutschiene, 3 Pol","Schneider",16,4,12,2.5,6.5,"Neozed Sicherungssockel D01, 3P, 16A,  400V, DIN-Schiene"]
["Sicherungsträger","Schraubsicherungssystem D 02/E18, einschl. Sicherung","R9J02163","auf Hutschiene, 1 Pol","Schneider",63,{"$f":"H90","v":7},7,5.5,12.5,"Neozed Sicherungssockel D02, 1P, 63A, 400V, DIN-Schiene"]
["Sicherungsträger",null,"R9J02363","auf Hutschiene, 3 Pol","Schneider",63,7,21,5.5,12.5,"Neozed Sicherungssockel D02, 3P, 63A, 400V, DIN-Schiene"]
["Sicherungsträger",null,"XNR663BN","SaS 60mm, 3 Pol","ABN",63,1.9666666666666668,5.9,5.5,7.4666666666666668,"D02-Reiterelement 63A mit 36mm Abdeckung 3p SaS 60mm EBM 32mm"]
["Sicherungsträger",null,"XNR663N",null,"ABN",63,{"$f":"H93/3","v":1.9666666666666668},5.9,5.5,{"$f":"G93+I93","v":7.4666666666666668},"D02-Reiterelement 63A mit 27mm Abdeckung 3p SaS 60mm EBM 32mm"]
["Sicherungsträger",null,"XNR363",null,"ABN",63,1.9666666666666668,5.9,5.5,7.4666666666666668,"Neozed-Element 63A 3p auf SaS 10mm CU Reiter-Sicherungselement E18"]
["Sicherungsträger",null,"XNR363-5",null,"ABN",63,1.9666666666666668,5.9,5.5,7.4666666666666668,"Neozed-Element 63A 3p auf SaS 5mm CU Reiter-Sicherungselement E18"]
["Sicherungsträger",null,"XTNR663N","SaS 60mm, 3 Pol","ABN",63,5,15,5.5,10.5,"D02-Lasttrennschalter 63A 3p SaS 60mm EBM 32/63mm max. 10 mm²"]
["Sicherungsträger",null,"XTNR663BN","SaS 60mm, 3 Pol","ABN",63,5,15,5.5,10.5,"D02-Lasttrennschalter 63A 3p blinkend SaS 60mm EBM 32mm"]
["Sicherungsträger","Schraubsicherungssystem D II/E27, einschl. Sicherung","E-XD126","Hutschiene","ABN","25",0.7,null,4.5,5.2,"Diazed-Element E27 kpl.m.Deck. 1pol., 25A, D2 Schelle/Schelle"]
["Sicherungsträger",null,"E-XDR325-5","SaS 60mm, 3 Pol","ABN",25,0.39999999999999997,1.2,4.5,4.9000000000000004,"Reitersicherungselement 25A 3p DII SAS 60mm f. 5-10mm CU (o.Abd.)"]
["Sicherungsträger",null,"XDR625N",null,"ABN",25,{"$f":"H100/3","v":0.39999999999999997},1.2,4.5,{"$f":"G100+I100","v":4.9000000000000004},"Reitersicherungselement 25A mit 42mm Abdeckung 3p DII SaS 60mm EBM 32mm"]
["Sicherungsträger","Schraubsicherungssystem D III/E33, einschl. Sicherung","E-XDR363-5","SaS 60mm, 3 Pol","ABN",63,3.3333333333333335,10,7,10.333333333333334,"Reitersicherungselement 63A 3p DIII SAS 60mm f. 5-10mm CU (o.Abd.)"]
["Sicherungsträger",null,"XDR663N",null,"ABN",63,{"$f":"H102/3","v":3.3333333333333335},10,7,{"$f":"G102+I102","v":10.333333333333334},"Reitersicherungselement 63A mit 57mm Abdeckung 3p DIII SaS 60mm EBM 32mm"]
["Sicherungsträger","Sicherungsunterteil NH00, einschl. Sicherung","HS434C","Hausanschlusskasten","ABN",100,4,12,6.6,{"$f":"G103+I103","v":10.6},"Kabel-Hausanschlusskasten KH00 K4 1x3NH00 V-Doppelklemme 10-95 mm² DIN43627"]
["Sicherungsträger",null,"HK334KL-J",null,"ABN",100,4,12,6.6,{"$f":"G104+I104","v":10.6},"Kabel-Hausanschlusskasten KH00 K3 245X415mm, Klarsicht_JM"]
["Sicherungsträger",null,"HK334KL",null,"ABN",100,4,12,6.6,10.6,"Kabel-Hausanschlusskasten KH00 K3 245x415mm Klarsicht"]
["Sicherungsträger",null,"HK335C-J",null,"ABN",100,4,12,6.6,10.6,"Kabel-Hausanschlusskasten KH00 KU5 NH00 100A, TN-S-Netz, 413x238x132mm"]
["Sicherungsträger",null,"HK334C",null,"ABN",100,4,12,6.6,{"$f":"G107+I107","v":10.6},"Hausanschlusskasten KH00 K3 1x3NH00 Zugang V-Klemme Abgang 3xStahlrahmenklemme"]
["Sicherungsträger",null,"HK334C-J",null,"ABN",100,4,12,6.6,{"$f":"G108+I108","v":10.6},"KH00 DIN43627 K3 1x3NH00 Zugang V-Klemme, Abgang 3x Stahlrahmenklemme_JM"]
["Sicherungsträger",null,"HK335C-U",null,"ABN",100,4,12,6.6,10.6,"Kabel-Hausanschlusskasten 5-pol.,1x3xNH00 bis 100A 10-95mm², 397x244x113mm"]
["Sicherungsträger",null,"HK864C","Hausanschlusskasten Doppel. MPL, 3Pol","ABN",100,4,24,6.6,{"$f":"G110+I110","v":10.6},"Kabel-Hausanschlusskasten K12 2x3xNH00 2x50-185 mm² 2x100A"]
["Sicherungsträger",null,"HK864C-J",null,"ABN",100,4,24,6.6,{"$f":"G111+I111","v":10.6},"Kabel-Hausanschlusskasten K12 2x3xNH00, 2x50-185qmm, 2x100A_JM"]
["Sicherungsträger",null,102000,"NH-Unterteil, 40mm SaS, 3Pol","ABN",160,6.333333333333333,19,11.2,17.533333333333331,"NH00-Sicherungsunterteil 3pol. für  40mm SaS Montage, Univ. Anschl. M8, EBM70mm"]
["Sicherungsträger",null,"ABNPE508F01",null,"ABN",160,{"$f":"H113/3","v":6.333333333333333},19,11.2,{"$f":"G113+I113","v":17.533333333333331},"NH00-Sicherungsunterteil 3pol auf 40mm SAS mit Uni-Anschl. M8"]
["Sicherungsträger",null,"XUS3-00",null,"ABN",160,4.7,{"$f":"3*G114","v":14.100000000000001},11.2,15.899999999999999,"NH-Unterteil Gr.00 3-polig Montage auf Sammelschienen"]
["Sicherungsträger",null,"XUS1-00",null,"ABN",160,{"$f":"H115/3","v":4.7},14.1,11.2,{"$f":"G115+I115","v":15.899999999999999},"NH-Unterteil Gr.00 1p SaS Montage"]
["Sicherungsträger",null,"XUS6-00","NH-Unterteil Doppel, 40mm SaS, 3Pol","ABN",160,3.6,10.8,11.2,14.799999999999999,"NH-Unterteil Gr.00 2x3p SaS Montage"]
["Sicherungsträger",null,"XUM1-00","NH-Unterteil, MPL, 3Pol","ABN",160,{"$f":"H117/3","v":4.2},12.6,11.2,{"$f":"G117+I117","v":15.399999999999999},"NH-Unterteil Gr.00 1p Montageplatte"]
["Sicherungsträger","Sicherungsunterteil NH 1, einschl. Sicherung","HS837C","Hausanschlusskasten. MPL, 3Pol","ABN","250",5,null,17,22,"Kabel-Hausanschlusskasten K12 Transparent 1x3xNH2/1 2x50-185 mm² 250A"]
["Sicherungsträger",null,100499,null,"ABN","250",5,null,17,22,"Kabelanschlusskasten KH1 K12 3xNH2 EFEN 93412-0003-SNH"]
["Sicherungsträger",null,"HK837C",null,"ABN","250",5,null,17,22,"Kabel-Hausanschlusskasten K12 1x3xNH2/1"]
["Sicherungsträger",null,"E-XUS3-1","NH-Unterteil auf 40mm SaS, 3Pol","ABN",250,{"$f":"H121/3","v":7.333333333333333},22,17,{"$f":"G121+I121","v":24.333333333333332},"NH-Reiter-Sicherungsunterteil Gr.1, 3pol. 40mm SS 3pol., 250A, M10"]
["Sicherungsträger",null,"XUS3-1-60","NH-Unterteil auf 60mm SaS, 3Pol","ABN",250,10.47,31.4,17,27.47,"NH-Unterteil Gr.1 3p SaS 60mm Montage"]
["Sicherungsträger",null,"XUM3-1","NH-Unterteil MPL, 3Pol","ABN",250,4.333333333333333,13,17,21.333333333333332,"NH-Unterteil Gr.1 250A 3p Montageplatte M10"]
["Sicherungsträger","Sicherungsunterteil NH 2, einschl. Sicherung","E-XUS3-2","NH-Unterteil auf 40mm SaS, 3Pol","ABN",400,{"$f":"H124/3","v":18.666666666666668},56,29,{"$f":"G124+I124","v":47.666666666666671},"NH-Reiter-Sicherungsunterteil Gr.2, 3pol. 40mm SS  3pol., 400A, M10"]
["Sicherungsträger",null,"ABNPE520F01",null,"ABN",400,{"$f":"H125/3","v":18.666666666666668},56,29,{"$f":"G125+I125","v":47.666666666666671},"NH2-Sicherungsunterteil 3pol auf 40mm SAS mit Uni-Anschl. M10"]
["Sicherungsträger",null,"XUS3-2-60","NH-Unterteil auf 60mm SaS, 3Pol","ABN",400,{"$f":"H126/3","v":18.666666666666668},56,29,{"$f":"G126+I126","v":47.666666666666671},"NH-Unterteil Gr.2 3p SaS 60mm Montage"]
["Sicherungsträger",null,"E-XUM320JM","NH-Unterteil MPL, 3Pol","ABN",400,{"$f":"H127/3","v":7},21,29,{"$f":"G127+I127","v":36},"NH-Unterteil Gr.2 1-polig U2-1IGZ/H mit Kontaktabd Jean Müller Art. Nr.: U2311301"]
["Sicherungsträger",null,"ABNPE320F01",null,"ABN",400,7,21,29,36,"NH2-Sicherungsunterteil 3pol mit Trennschottung Uni-Anschl. M10"]
["Sicherungsträger",null,"XUM3-2",null,"ABN",400,7,21,29,36,"NH-Unterteil Gr.2 3p Montageplatte M10 mit Nullleiterklemme"]
[null,null,null,null,null,null,null,null,null,0]
["Lasttrenschalter INS/INV","Lasttrenschalter INS/INV",null,null,null,null,null,null,null,0]
["Lasttrenschalter INS/INV","Lasttrennschalter (40 A)","Compact INS, 3 Pol",null,"Schneider",40,0.5,{"$f":"G132*3","v":1.5},null,0.5,"Compact INS, 3 Pol 40 A"]
["Lasttrenschalter INS/INV","Lasttrennschalter (63 A)","Compact INS, 3 Pol",null,"Schneider",63,1.2,{"$f":"G133*3","v":3.5999999999999996},null,1.2,"Compact INS, 3 Pol 63 A"]
["Lasttrenschalter INS/INV","Lasttrennschalter (100 A)","Compact INS, 3 Pol",null,"Schneider",100,1.9,5.6999999999999993,null,1.9,"Compact INS, 3 Pol 100 A"]
["Lasttrenschalter INS/INV",null,"Compact INV, 3 Pol",null,"Schneider",100,1.5,4.5,null,1.5,"Compact INV, 3 Pol 100 A"]
["Lasttrenschalter INS/INV","Lasttrennschalter (125 A)","Compact INS, 3 Pol",null,"Schneider",125,3.1,9.3000000000000007,null,3.1,"Compact INS, 3 Pol 125 A"]
["Lasttrenschalter INS/INV","Lasttrennschalter (160 A)","Compact INS, 3 Pol",null,"Schneider",160,5.0999999999999996,15.299999999999999,null,5.0999999999999996,"Compact INS, 3 Pol 160 A"]
["Lasttrenschalter INS/INV",null,"Compact INV, 3 Pol",null,"Schneider",160,4,12,null,4,"Compact INV, 3 Pol 160 A"]
["Lasttrenschalter INS/INV","Lasttrennschalter (250 A)","Compact INS/INV, 3 Pol",null,"Schneider",250,9.5,28.5,null,9.5,"Compact INS/INV, 3 Pol 250 A"]
["Lasttrenschalter INS/INV","Lasttrennschalter (400 A)","Compact INS/INV, 3 Pol",null,"Schneider",400,9.6,28.799999999999997,null,9.6,"Compact INS/INV, 3 Pol 400 A"]
["Lasttrenschalter INS/INV","Lasttrennschalter (630 A)","Compact INS/INV, 3 Pol",null,"Schneider",630,24,72,null,24,"Compact INS/INV, 3 Pol 630 A"]
["Lasttrenschalter INS/INV","Lasttrennschalter (800 A)","Compact INS/INV, 3 Pol",null,"Schneider",800,16,48,null,16,"Compact INS/INV, 3 Pol 800 A"]
["Lasttrenschalter INS/INV","Lasttrennschalter (1000 A)","Compact INS/INV, 3 Pol",null,"Schneider",1000,24,72,null,24,"Compact INS/INV, 3 Pol 1000 A"]
["Lasttrenschalter INS/INV","Lasttrennschalter (1250 A)","Compact INS/INV, 3 Pol",null,"Schneider",1250,38,114,null,38,"Compact INS/INV, 3 Pol 1250 A"]
["Lasttrenschalter INS/INV","Lasttrennschalter (1600 A)","Compact INS/INV, 3 Pol",null,"Schneider",1600,62,186,null,62,"Compact INS/INV, 3 Pol 1600 A"]
["Lasttrenschalter INS/INV","Lasttrennsch. INS63,3P, 63A/690V AC/250V DC  ,Drehantrieb schwarz",28902,null,"Schneider",63,1.2,null,null,{"$f":"G146+I146","v":1.2},"Lasttrennsch. INS63,3P, 63A/690V AC/250V DC  ,Drehantrieb schwarz"]
["Lasttrenschalter INS/INV","Lasttrennsch. INS100,3P, 100A/690V AC/250V DC,Drehantrieb schwarz",28908,null,"Schneider",100,1.9,null,null,1.9,"Lasttrennsch. INS100,3P, 100A/690V AC/250V DC,Drehantrieb schwarz"]
["Lasttrenschalter INS/INV","Lasttrennsch. INS100,4P, 100A/690V AC/250V DC,Drehantrieb schwarz",28909,null,"Schneider",100,1.9,null,null,1.9,"Lasttrennsch. INS100,4P, 100A/690V AC/250V DC,Drehantrieb schwarz"]
["Lasttrenschalter INS/INV","Lasttrennschalter 125A 3-polig montage auf Hutschiene mit Griff",28910,null,"Schneider",125,3.1,null,null,3.1,"Lasttrennschalter 125A 3-polig montage auf Hutschiene mit Griff"]
["Lasttrenschalter INS/INV","Lasttrennsch. INS125,4P, 125A/690V AC/250V DC,Drehantrieb schwarz",28911,null,"Schneider",125,3.1,null,null,3.1,"Lasttrennsch. INS125,4P, 125A/690V AC/250V DC,Drehantrieb schwarz"]
["Lasttrenschalter INS/INV","Lasttrennsch. INS160,3P, 160A/690V AC/250V DC,Drehantrieb schwarz",28912,null,"Schneider",160,5.0999999999999996,null,null,5.0999999999999996,"Lasttrennsch. INS160,3P, 160A/690V AC/250V DC,Drehantrieb schwarz"]
["Lasttrenschalter INS/INV","Lasttrennsch. INS160,4P, 160A/690V AC/250V DC,Drehantrieb schwarz",28913,null,"Schneider",160,5.0999999999999996,null,null,5.0999999999999996,"Lasttrennsch. INS160,4P, 160A/690V AC/250V DC,Drehantrieb schwarz"]
["Lasttrenschalter INS/INV","Lasttrennsch. INS250,3P, 160A/690V AC/250V DC,Drehantrieb schwarz",31104,null,"Schneider",250,9.5,null,null,9.5,"Lasttrennsch. INS250,3P, 160A/690V AC/250V DC,Drehantrieb schwarz"]
["Lasttrenschalter INS/INV","Lasttrennsch. INS250,4P, 160A/690V AC/250V DC,Drehantrieb schwarz",31105,null,"Schneider",250,9.5,null,null,9.5,"Lasttrennsch. INS250,4P, 160A/690V AC/250V DC,Drehantrieb schwarz"]
["Lasttrenschalter INS/INV","Lasttrennschalter 250A 3-polig montage auf Traverse mit Griff",31106,null,"Schneider",250,9.5,null,null,9.5,"Lasttrennschalter 250A 3-polig montage auf Traverse mit Griff"]
["Lasttrenschalter INS/INV","Lasttrennsch. INS250,4P, 250A/690V AC/250V DC,Drehantrieb schwarz",31107,null,"Schneider",250,9.5,null,null,9.5,"Lasttrennsch. INS250,4P, 250A/690V AC/250V DC,Drehantrieb schwarz"]
["Lasttrenschalter INS/INV","Lasttrennsch. INS400,3P, 400A/690V AC/250V DC,Drehantrieb schwarz",31110,null,"Schneider",400,9.6,null,null,9.6,"Lasttrennsch. INS400,3P, 400A/690V AC/250V DC,Drehantrieb schwarz"]
["Lasttrenschalter INS/INV","Lasttrennsch. INS400,4P, 400A/690V AC/250V DC,Drehantrieb schwarz",31111,null,"Schneider",400,9.6,null,null,9.6,"Lasttrennsch. INS400,4P, 400A/690V AC/250V DC,Drehantrieb schwarz"]
["Lasttrenschalter INS/INV","Lasttrennsch. INS630,3P, 630A/690V AC/250V DC,Drehantrieb schwarz",31114,null,"Schneider",630,24,null,null,24,"Lasttrennsch. INS630,3P, 630A/690V AC/250V DC,Drehantrieb schwarz"]
["Lasttrenschalter INS/INV","Lasttrennsch. INS630,4P, 630A/690V AC/250V DC,Drehantrieb schwarz",31115,null,"Schneider",630,24,null,null,24,"Lasttrennsch. INS630,4P, 630A/690V AC/250V DC,Drehantrieb schwarz"]
["Lasttrenschalter INS/INV","Manueller Netzumschalter mit ComPact INS250 4P 160A Festeinbau",31145,null,"Schneider",250,9.5,null,null,{"$f":"G161+I161","v":9.5},"Manueller Netzumschalter mit ComPact INS250 4P 160A Festeinbau"]
["Lasttrenschalter INS/INV","Manueller Netzumschalter, Interpact INS250 4P, 250A Festeinbau",31147,null,"Schneider",250,9.5,null,null,9.5,"Manueller Netzumschalter, Interpact INS250 4P, 250A Festeinbau"]
["Lasttrenschalter INS/INV","Manueller Netzumschalter mitComPact INS400 4P 400AFesteinbau",31151,null,"Schneider",400,9.6,null,null,9.6,"Manueller Netzumschalter mitComPact INS400 4P 400AFesteinbau"]
["Lasttrenschalter INS/INV","Manueller Netzumschalter, Interpact INS630, 4P, 630A Festeinbau",31155,null,"Schneider",630,24,null,null,24,"Manueller Netzumschalter, Interpact INS630, 4P, 630A Festeinbau"]
["Lasttrenschalter INS/INV","Gussgekapselter Trennschalter Interpact INS1000, 3p, 1000A",31332,null,"Schneider",1000,24,null,null,24,"Gussgekapselter Trennschalter Interpact INS1000, 3p, 1000A"]
["Lasttrenschalter INS/INV","Trennschalter Interpact INS1250, 3p, 1250A",31334,null,"Schneider",1250,38,null,null,38,"Trennschalter Interpact INS1250, 3p, 1250A"]
[null,null,null,null,null,null,null,null,null,0]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrenschalter/Leistungstrenner Compact NSX/NS"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter 160A 3-polig  Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE302S41",null,"Schneider",160,8.5500000000000007,null,null,{"$f":"G169+I169","v":8.5500000000000007},"Lasttrennschalter 160A 3-polig  Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter 250A 3-polig  Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE303S41",null,"Schneider",250,14.52,null,null,14.52,"Lasttrennschalter 250A 3-polig  Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter 400A 3-polig  Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE304S41",null,"Schneider",400,12.29,null,null,12.29,"Lasttrennschalter 400A 3-polig  Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter 1250A 3-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE308S41",null,"Schneider",1250,14.67,null,null,14.67,"Lasttrennschalter 1250A 3-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter 160A 4-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE402S41",null,"Schneider",160,8.5500000000000007,null,null,8.5500000000000007,"Lasttrennschalter 160A 4-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter 630A 4-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE405S41",null,"Schneider",630,25,null,null,25,"Lasttrennschalter 630A 4-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter 250A 4-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE403S41",null,"Schneider",250,14.52,null,null,14.52,"Lasttrennschalter 250A 4-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter 1250A 4-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE408S41",null,"Schneider",1250,14.67,null,null,14.67,"Lasttrennschalter 1250A 4-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter 400A 4-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE404S41",null,"Schneider",400,12.29,null,null,12.29,"Lasttrennschalter 400A 4-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter 1000A 4-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE407S41",null,"Schneider",1000,7.3,null,null,7.3,"Lasttrennschalter 1000A 4-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter 1600A 4-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE409S41",null,"Schneider",1600,24.67,null,null,24.67,"Lasttrennschalter 1600A 4-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter 160A 3-polig Montiert auf Traverse mit Griff","XLTS30160",null,"Schneider",250,9.5,null,null,9.5,"Lasttrennschalter 160A 3-polig Montiert auf Traverse mit Griff"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter 630A 3-polig  Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE305S41",null,"Schneider",630,25,null,null,25,"Lasttrennschalter 630A 3-polig  Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter 800A 3-polig manuelle Betätigung","PE306S40",null,"Schneider",800,5,null,null,5,"Lasttrennschalter 800A 3-polig manuelle Betätigung"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter 800A 3-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE306S41",null,"Schneider",800,5,null,null,5,"Lasttrennschalter 800A 3-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter 1000A 3-polig manuelle Betätigung","PE307S40",null,"Schneider",1000,7.33,null,null,7.33,"Lasttrennschalter 1000A 3-polig manuelle Betätigung"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter 1000A 3-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE307S41",null,"Schneider",1000,7.33,null,null,7.33,"Lasttrennschalter 1000A 3-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter 1250A 3-polig manuelle Betätigung","PE308S40",null,"Schneider",1250,14.67,null,null,14.67,"Lasttrennschalter 1250A 3-polig manuelle Betätigung"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter 1600A 3-polig manuelle Betätigung","PE309S40",null,"Schneider",1600,24.67,null,null,24.67,"Lasttrennschalter 1600A 3-polig manuelle Betätigung"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter 1600A 3-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE309S41",null,"Schneider",1600,24.67,null,null,24.67,"Lasttrennschalter 1600A 3-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter 1000A 4-polig manuelle Betätigung","PE407S40",null,"Schneider",1000,7.33,null,null,7.33,"Lasttrennschalter 1000A 4-polig manuelle Betätigung"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter 1250A 4-polig manuelle Betätigung","PE408S40",null,"Schneider",1250,14.67,null,null,14.67,"Lasttrennschalter 1250A 4-polig manuelle Betätigung"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter 1600A 4-polig manuelle Betätigung","PE409S40",null,"Schneider",1600,24.67,null,null,24.67,"Lasttrennschalter 1600A 4-polig manuelle Betätigung"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter ComPacT NS630b NA 3P, 630 A / 690 V AC, Kipphebel","C063S3FM",null,"Schneider",630,3.33,null,null,3.33,"Lasttrennschalter ComPacT NS630b NA 3P, 630 A / 690 V AC, Kipphebel"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter ComPacT NS630b NA 4P, 630 A / 690 V AC, Kipphebel","C063S4FM",null,"Schneider",630,3.33,null,null,3.33,"Lasttrennschalter ComPacT NS630b NA 4P, 630 A / 690 V AC, Kipphebel"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter 800A 4-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE406S41",null,"Schneider",800,5,null,null,5,"Lasttrennschalter 800A 4-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","ComPacT SWITCH NSX630NA AC 4P4D 630A  ","C634630S",null,"Schneider",630,25,null,null,25,"ComPacT SWITCH NSX630NA AC 4P4D 630A  "]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","ComPacT SWITCH NSX160NA AC 4P 160A  ","C164160S",null,"Schneider",160,8.5500000000000007,null,null,8.5500000000000007,"ComPacT SWITCH NSX160NA AC 4P 160A  "]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","ComPacT SWITCH NSX250NA AC 3P 250A  ","C253250S",null,"Schneider",250,14.52,null,null,14.52,"ComPacT SWITCH NSX250NA AC 3P 250A  "]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","ComPacT SWITCH NSX250NA AC 4P 250A  ","C254250S",null,"Schneider",250,14.52,null,null,14.52,"ComPacT SWITCH NSX250NA AC 4P 250A  "]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","ComPacT SWITCH NSX630NA AC 3P3D 630A  ","C633630S",null,"Schneider",630,25,null,null,25,"ComPacT SWITCH NSX630NA AC 3P3D 630A  "]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","ComPacT SWITCH NSX160NA AC 3P 160A  ","C163160S",null,"Schneider",160,8.5500000000000007,null,null,8.5500000000000007,"ComPacT SWITCH NSX160NA AC 3P 160A  "]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","ComPacT SWITCH NSX400NA AC 3P3D 400A  ","C403400S",null,"Schneider",400,12.29,null,null,12.29,"ComPacT SWITCH NSX400NA AC 3P3D 400A  "]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","ComPacT SWITCH NSX400NA AC 4P4D 400A  ","C404400S",null,"Schneider",400,12.29,null,null,12.29,"ComPacT SWITCH NSX400NA AC 4P4D 400A  "]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter ComPacT NS800 NA 3P, 800 A / 690 V AC, Kipphebel","C080S3FM",null,"Schneider",800,5,null,null,5,"Lasttrennschalter ComPacT NS800 NA 3P, 800 A / 690 V AC, Kipphebel"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter ComPacT NS800 NA 4P, 800 A / 690 V AC, Kipphebel","C080S4FM",null,"Schneider",800,5,null,null,5,"Lasttrennschalter ComPacT NS800 NA 4P, 800 A / 690 V AC, Kipphebel"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter ComPacT NS1000 NA 3P, 1.000 A / 690 V AC, Kipphebel","C100S3FM",null,"Schneider",1000,7.33,null,null,7.33,"Lasttrennschalter ComPacT NS1000 NA 3P, 1.000 A / 690 V AC, Kipphebel"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter ComPacT NS1000 NA 4P, 1.000 A / 690 V AC, Kipphebel","C100S4FM",null,"Schneider",1000,7.33,null,null,7.33,"Lasttrennschalter ComPacT NS1000 NA 4P, 1.000 A / 690 V AC, Kipphebel"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter ComPacT NS1250 NA 3P, 1.250 A / 690 V AC, Kipphebel","C125S3FM",null,"Schneider",1250,14.67,null,null,14.67,"Lasttrennschalter ComPacT NS1250 NA 3P, 1.250 A / 690 V AC, Kipphebel"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter ComPacT NS1250 NA 4P, 1.250 A / 690 V AC, Kipphebel","C125S4FM",null,"Schneider",1250,14.67,null,null,14.67,"Lasttrennschalter ComPacT NS1250 NA 4P, 1.250 A / 690 V AC, Kipphebel"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","Lasttrennschalter ComPacT NS1600 NA 3P, 1.600 A / 690 V AC, Kipphebel","C160S3FM",null,"Schneider",1600,24.67,null,null,24.67,"Lasttrennschalter ComPacT NS1600 NA 3P, 1.600 A / 690 V AC, Kipphebel"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","ComPacT NS800N, 3P, 800 A max. Ausschaltverm. 50 kA","C080N3FM",null,"Schneider",800,5,null,null,{"$f":"G210+I210","v":5},"ComPacT NS800N, 3P, 800 A max. Ausschaltverm. 50 kA"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","ComPacT NS800N, 4P, 800 A max. Ausschaltverm. 50 kA","C080N4FM",null,"Schneider",800,5,null,null,5,"ComPacT NS800N, 4P, 800 A max. Ausschaltverm. 50 kA"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","ComPacT NS1000N, 3P, 1.000 A max. Ausschaltverm. 50 kA","C100N3FM",null,"Schneider",1000,7.33,null,null,7.33,"ComPacT NS1000N, 3P, 1.000 A max. Ausschaltverm. 50 kA"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","ComPacT NS1000N, 4P, 1.000 A max. Ausschaltverm. 50 kA","C100N4FM",null,"Schneider",1000,7.33,null,null,7.33,"ComPacT NS1000N, 4P, 1.000 A max. Ausschaltverm. 50 kA"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","ComPacT NS1250N, 3P, 1.250 A max. Ausschaltverm. 50 kA","C125N3FM",null,"Schneider",1250,14.67,null,null,14.67,"ComPacT NS1250N, 3P, 1.250 A max. Ausschaltverm. 50 kA"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","ComPacT NS1250N, 4P, 1.250 A  max. Ausschaltverm. 50 kA","C125N4FM",null,"Schneider",1250,14.67,null,null,14.67,"ComPacT NS1250N, 4P, 1.250 A  max. Ausschaltverm. 50 kA"]
["Lasttrenschalter/Leistungstrenner Compact NSX/NS","ComPacT NS1600N, 3P, 1.600 A max. Ausschaltverm. 50 kA","C160N3FM",null,"Schneider",1600,24.67,null,null,24.67,"ComPacT NS1600N, 3P, 1.600 A max. Ausschaltverm. 50 kA"]
[null,null,null,null,null,null,null,null,null,0]
["Leistungsschalter Compact NSX/NS","Leistungsschalter Compact NSX/NS",null,null,null,null,null,null,null,0]
["Leistungsschalter Compact NSX/NS","Leistungsschalter (16 A)","Compact NSXm, TM-D trip unit, 3 Pol",null,"Schneider",16,2.2999999999999998,{"$f":"G219*3","v":6.8999999999999995},null,2.2999999999999998,"Compact NSXm, TM-D trip unit, 3 Pol 16 A"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter (25 A)","Compact NSXm, TM-D trip unit, 3 Pol",null,"Schneider",25,2.8,8.3999999999999986,null,{"$f":"G220+I220","v":2.8},"Compact NSXm, TM-D trip unit, 3 Pol 25 A"]
["Leistungsschalter Compact NSX/NS",null,"Compact NSXm, Micrologic Vigi 4.1, 3 Pol",null,"Schneider",25,1.5,4.5,null,1.5,"Compact NSXm, Micrologic Vigi 4.1, 3 Pol 25 A"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter (32 A)","Compact NSXm, TM-D trip unit, 3 Pol",null,"Schneider",32,3.3,9.8999999999999986,null,3.3,"Compact NSXm, TM-D trip unit, 3 Pol 32 A"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter (40 A)","Compact NSXm, TM-D trip unit, 3 Pol",null,"Schneider",40,3.8,11.399999999999999,null,3.8,"Compact NSXm, TM-D trip unit, 3 Pol 40 A"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter (50 A)","Compact NSXm, TM-D trip unit, 3 Pol",null,"Schneider",50,4.5999999999999996,13.799999999999999,null,4.5999999999999996,"Compact NSXm, TM-D trip unit, 3 Pol 50 A"]
["Leistungsschalter Compact NSX/NS",null,"Compact NSXm, Micrologic Vigi 4.1, 3 Pol",null,"Schneider",50,1.2,3.5999999999999996,null,1.2,"Compact NSXm, Micrologic Vigi 4.1, 3 Pol 50 A"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter (63 A)","Compact NSXm, TM-D trip unit, 3 Pol",null,"Schneider",63,5.7,17.100000000000001,null,5.7,"Compact NSXm, TM-D trip unit, 3 Pol 63 A"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter (80 A)","Compact NSXm, TM-D trip unit, 3 Pol",null,"Schneider",80,5.8,17.399999999999999,null,5.8,"Compact NSXm, TM-D trip unit, 3 Pol 80 A"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter (100 A)","Compact NSX, TM-D/TM-G trip unit, 3 Pol",null,"Schneider",100,8.8000000000000007,{"$f":"G228*3","v":26.400000000000002},null,8.8000000000000007,"Compact NSX, TM-D/TM-G trip unit, 3 Pol 100 A"]
["Leistungsschalter Compact NSX/NS",null,"Compact NSX,MA/1.3-M trip unit, 3 Pol",null,"Schneider",100,5.2,{"$f":"G229*3","v":15.600000000000001},null,5.2,"Compact NSX,MA/1.3-M trip unit, 3 Pol 100 A"]
["Leistungsschalter Compact NSX/NS",null,"Compact NSX,MicroLogic2.2/5.2/6.2, 3 Pol",null,"Schneider",100,4.7,14.100000000000001,null,4.7,"Compact NSX,MicroLogic2.2/5.2/6.2, 3 Pol 100 A"]
["Leistungsschalter Compact NSX/NS",null,"Compact NSX,MicroLogic 4.2/7.2,3 Pol",null,"Schneider",100,{"$f":"H231/3","v":5.5},16.5,null,5.5,"Compact NSX,MicroLogic 4.2/7.2,3 Pol 100 A"]
["Leistungsschalter Compact NSX/NS",null,"Compact NSXm, TM-D trip unit, 3 Pol",null,"Schneider",100,7.5,22.5,null,7.5,"Compact NSXm, TM-D trip unit, 3 Pol 100 A"]
["Leistungsschalter Compact NSX/NS",null,"Compact NSXm, Micrologic Vigi 4.1, 3 Pol",null,"Schneider",100,4.8,14.399999999999999,null,4.8,"Compact NSXm, Micrologic Vigi 4.1, 3 Pol 100 A"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter (125A)","Compact NSXm, TM-D trip unit, 3 Pol",null,"Schneider",125,9.3000000000000007,27.900000000000002,null,9.3000000000000007,"Compact NSXm, TM-D trip unit, 3 Pol 125 A"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter (160 A)","Compact NSX, TM-D/TM-G trip unit, 3 Pol",null,"Schneider",160,13.95,41.849999999999994,null,13.95,"Compact NSX, TM-D/TM-G trip unit, 3 Pol 160 A"]
["Leistungsschalter Compact NSX/NS",null,"Compact NSX,MA/1.3-M trip unit, 3 Pol",null,"Schneider",160,8.5500000000000007,25.650000000000002,null,8.5500000000000007,"Compact NSX,MA/1.3-M trip unit, 3 Pol 160 A"]
["Leistungsschalter Compact NSX/NS",null,"Compact NSX,MicroLogic2.2/5.2/6.2, 3 Pol",null,"Schneider",160,9.1999999999999993,27.599999999999998,null,9.1999999999999993,"Compact NSX,MicroLogic2.2/5.2/6.2, 3 Pol 160 A"]
["Leistungsschalter Compact NSX/NS",null,"Compact NSX,MicroLogic 4.2/7.2,3 Pol",null,"Schneider",160,11.5,34.6,null,11.5,"Compact NSX,MicroLogic 4.2/7.2,3 Pol 160 A"]
["Leistungsschalter Compact NSX/NS",null,"Compact NSXm, TMD",null,"Schneider",160,13.7,{"$f":"G239*3","v":41.099999999999994},null,{"$f":"G239+I239","v":13.7},"Compact NSXm, TMD 160 A"]
["Leistungsschalter Compact NSX/NS",null,"Compact NSXm, Micrologic Vigi 4.1, 3 Pol",null,"Schneider",160,12.3,36.900000000000006,null,12.3,"Compact NSXm, Micrologic Vigi 4.1, 3 Pol 160 A"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter (250 A)","Compact NSX, TM-D/TM-G trip unit, 3 Pol",null,"Schneider",250,18.75,56.25,null,18.75,"Compact NSX, TM-D/TM-G trip unit, 3 Pol 250 A"]
["Leistungsschalter Compact NSX/NS",null,"Compact NSX,MA/1.3-M trip unit, 3 Pol",null,"Schneider",250,14.52,43.56,null,14.52,"Compact NSX,MA/1.3-M trip unit, 3 Pol 250 A"]
["Leistungsschalter Compact NSX/NS",null,"Compact NSX,MicroLogic2.2/5.2/6.2, 3 Pol",null,"Schneider",250,17.600000000000001,52.800000000000004,null,17.600000000000001,"Compact NSX,MicroLogic2.2/5.2/6.2, 3 Pol 250 A"]
["Leistungsschalter Compact NSX/NS",null,"Compact NSX,MicroLogic 4.2/7.2,3 Pol",null,"Schneider",250,{"$f":"H244/3","v":23.533333333333331},70.599999999999994,null,23.533333333333331,"Compact NSX,MicroLogic 4.2/7.2,3 Pol 250 A"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter (400 A)","Compact NSX,MA/1.3-M trip unit, 3 Pol",null,"Schneider",400,12.29,36.869999999999997,null,12.29,"Compact NSX,MA/1.3-M trip unit, 3 Pol 400 A"]
["Leistungsschalter Compact NSX/NS",null,"Compact NSX, MicroLogic 2.3/5.3/6.3, 3 Pol",null,"Schneider",400,19.2,57.599999999999994,null,19.2,"Compact NSX, MicroLogic 2.3/5.3/6.3, 3 Pol 400 A"]
["Leistungsschalter Compact NSX/NS",null,"Compact NSX, MicroLogic 4.3/7.3, 3 Pol",null,"Schneider",400,{"$f":"H247/3","v":24.533333333333331},73.599999999999994,null,24.533333333333331,"Compact NSX, MicroLogic 4.3/7.3, 3 Pol 400 A"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter (630 A)","Compact NSX,MA/1.3-M trip unit, 3 Pol",null,"Schneider",630,25,75,null,25,"Compact NSX,MA/1.3-M trip unit, 3 Pol 630 A"]
["Leistungsschalter Compact NSX/NS",null,"Compact NSX, MicroLogic 2.3/5.3/6.3, 3 Pol",null,"Schneider",630,39.700000000000003,119.10000000000001,null,39.700000000000003,"Compact NSX, MicroLogic 2.3/5.3/6.3, 3 Pol 630 A"]
["Leistungsschalter Compact NSX/NS",null,"Compact NSX, MicroLogic 4.3/7.3, 3 Pol",null,"Schneider",630,{"$f":"H250/3","v":52.933333333333337},158.80000000000001,null,52.933333333333337,"Compact NSX, MicroLogic 4.3/7.3, 3 Pol 630 A"]
["Leistungsschalter Compact NSX/NS",null,"Compact NS, 3 Pol",null,"Schneider",630,{"$f":"H251/3","v":3.3333333333333335},10,null,3.3333333333333335,"Compact NS, 3 Pol 630 A"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter (800 A)","Compact NS, 3 Pol",null,"Schneider",800,5,15,null,5,"Compact NS, 3 Pol 800 A"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter (1000 A)","Compact NS, 3 Pol",null,"Schneider",1000,7.333333333333333,22,null,7.333333333333333,"Compact NS, 3 Pol 1000 A"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter (1250 A)","Compact NS, 3 Pol",null,"Schneider",1250,14.666666666666666,44,null,14.666666666666666,"Compact NS, 3 Pol 1250 A"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter (1600 A)","Compact NS, 3 Pol",null,"Schneider",1600,24.666666666666668,74,null,24.666666666666668,"Compact NS, 3 Pol 1600 A"]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX100B 25kA AC 4P4D 80A TMD ","C10B4TM080",null,"Schneider",80,8.77,null,null,{"$f":"G256+I256","v":8.77},"ComPacT BREAKER NSX100B 25kA AC 4P4D 80A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX100F 36kA AC 3P3D 100A TMD ","C10F3TM100",null,"Schneider",100,8.8000000000000007,null,null,8.8000000000000007,"ComPacT BREAKER NSX100F 36kA AC 3P3D 100A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX100F 36kA AC 4P4D 100A 2.2 ","C10F42D100",null,"Schneider",100,4.7,null,null,4.7,"ComPacT BREAKER NSX100F 36kA AC 4P4D 100A 2.2 "]
["Leistungsschalter Compact NSX/NS","Leistungsschalter NSX/NS+1472:1490","C11B3TM025L",null,"Schneider",25,2.8,null,null,2.8,"ComPacT BREAKER NSXm100B 25kA AC 3P 25A TMD ELINK"]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSXm100B 25kA AC 3P 40A TMD ELINK","C11B3TM040L",null,"Schneider",40,3.8,null,null,3.8,"ComPacT BREAKER NSXm100B 25kA AC 3P 40A TMD ELINK"]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSXm100B 25kA AC 3P 63A TMD ELINK","C11B3TM063L",null,"Schneider",63,5.7,null,null,5.7,"ComPacT BREAKER NSXm100B 25kA AC 3P 63A TMD ELINK"]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSXm100B 25kA AC 3P 80A TMD ELINK","C11B3TM080L",null,"Schneider",80,5.8,null,null,5.8,"ComPacT BREAKER NSXm100B 25kA AC 3P 80A TMD ELINK"]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSXm100F 36kA AC 3P 63A TMD ELINK","C11F3TM063L",null,"Schneider",63,5.7,null,null,5.7,"ComPacT BREAKER NSXm100F 36kA AC 3P 63A TMD ELINK"]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSXm160B 25kA AC 3P 160A TMD ELINK","C12B3TM160L",null,"Schneider",160,13.7,null,null,13.7,"ComPacT BREAKER NSXm160B 25kA AC 3P 160A TMD ELINK"]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX160B 25kA AC 3P 160A 2.2 ","C16B32D160",null,"Schneider",160,9.1999999999999993,null,null,9.1999999999999993,"ComPacT BREAKER NSX160B 25kA AC 3P 160A 2.2 "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX160F 36kA AC 3P3D 160A 2.2 ","C16F32D160",null,"Schneider",160,9.1999999999999993,null,null,9.1999999999999993,"ComPacT BREAKER NSX160F 36kA AC 3P3D 160A 2.2 "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX160F 36kA AC 3P3D 125A TMD ","C16F3TM125",null,"Schneider",160,10.78,null,null,10.78,"ComPacT BREAKER NSX160F 36kA AC 3P3D 125A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX160F 36kA AC 3P3D 160A TMD ","C16F3TM160",null,"Schneider",160,13.95,null,null,13.95,"ComPacT BREAKER NSX160F 36kA AC 3P3D 160A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX160F 36kA AC 4P4D 160A 2.2 ","C16F42D160",null,"Schneider",160,9.1999999999999993,null,null,9.1999999999999993,"ComPacT BREAKER NSX160F 36kA AC 4P4D 160A 2.2 "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX160F 36kA AC 4P4D 160A TMD ","C16F4TM160",null,"Schneider",160,13.95,null,null,13.95,"ComPacT BREAKER NSX160F 36kA AC 4P4D 160A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250B 25kA AC 3P 250A 2.2 ","C25B32D250",null,"Schneider",250,17.600000000000001,null,null,17.600000000000001,"ComPacT BREAKER NSX250B 25kA AC 3P 250A 2.2 "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250B 25kA AC 4P4D 250A TMD ","C25B4TM250",null,"Schneider",250,18.75,null,null,18.75,"ComPacT BREAKER NSX250B 25kA AC 4P4D 250A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250F 36kA AC 3P3D 250A 2.2 ","C25F32D250",null,"Schneider",250,17.600000000000001,null,null,17.600000000000001,"ComPacT BREAKER NSX250F 36kA AC 3P3D 250A 2.2 "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250F 36kA AC 3P3D 250A TMD ","C25F3TM250",null,"Schneider",250,18.75,null,null,18.75,"ComPacT BREAKER NSX250F 36kA AC 3P3D 250A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250F 36kA AC 4P4D 250A 2.2 ","C25F42D250",null,"Schneider",250,17.600000000000001,null,null,17.600000000000001,"ComPacT BREAKER NSX250F 36kA AC 4P4D 250A 2.2 "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250N 50kA AC 4P4D 250A TMD ","C25N4TM250",null,"Schneider",250,18.75,null,null,18.75,"ComPacT BREAKER NSX250N 50kA AC 4P4D 250A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX400F 36kA AC 3P3D 400A 2.3 ","C40F32D400",null,"Schneider",400,12.29,null,null,12.29,"ComPacT BREAKER NSX400F 36kA AC 3P3D 400A 2.3 "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX400F 36kA AC 4P4D 400A 2.3 ","C40F42D400",null,"Schneider",400,19.2,null,null,19.2,"ComPacT BREAKER NSX400F 36kA AC 4P4D 400A 2.3 "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX400N 50kA AC 3P3D 400A 2.3 ","C40N32D400",null,"Schneider",400,19.2,null,null,19.2,"ComPacT BREAKER NSX400N 50kA AC 3P3D 400A 2.3 "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX400N 50kA AC 4P4D 400A 2.3 ","C40N42D400",null,"Schneider",400,19.2,null,null,19.2,"ComPacT BREAKER NSX400N 50kA AC 4P4D 400A 2.3 "]
["Leistungsschalter Compact NSX/NS","ComPacT TRIP UNIT NSX630 AC 4P4D 630A 2.3 ","C6342D630",null,"Schneider",630,39.700000000000003,null,null,39.700000000000003,"ComPacT TRIP UNIT NSX630 AC 4P4D 630A 2.3 "]
["Leistungsschalter Compact NSX/NS","ComPacT TRIP UNIT NSX630 AC 4P4D 630A 5.3E ","C6345E630",null,"Schneider",630,39.700000000000003,null,null,39.700000000000003,"ComPacT TRIP UNIT NSX630 AC 4P4D 630A 5.3E "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX630N 50kA AC 3P3D 630A 2.3 ","C63N32D630",null,"Schneider",630,39.700000000000003,null,null,39.700000000000003,"ComPacT BREAKER NSX630N 50kA AC 3P3D 630A 2.3 "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX630N 50kA AC 4P4D 630A 2.3 ","C63N42D630",null,"Schneider",630,39.700000000000003,null,null,39.700000000000003,"ComPacT BREAKER NSX630N 50kA AC 4P4D 630A 2.3 "]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 160A 36kA 3-polig  Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE302S61",null,"Schneider",160,9.1999999999999993,null,null,9.1999999999999993,"Leistungsschalter 160A 36kA 3-polig  Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 250A 36kA 3-polig  Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE303S61",null,"Schneider",250,17.600000000000001,null,null,17.600000000000001,"Leistungsschalter 250A 36kA 3-polig  Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 400A 50kA 3-polig  Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE304S61",null,"Schneider",400,19.2,null,null,19.2,"Leistungsschalter 400A 50kA 3-polig  Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 630A 50kA 3-polig  Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE305S61",null,"Schneider",630,25,null,null,25,"Leistungsschalter 630A 50kA 3-polig  Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 800A 3-polig, Micro. 2.0 manuelle Betätigung","PE306S60",null,"Schneider",630,39.700000000000003,null,null,39.700000000000003,"Leistungsschalter 800A 3-polig, Micro. 2.0 manuelle Betätigung"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 1000A 3-polig, Micro. 2.0 manuelle Betätigung","PE307S60",null,"Schneider",1000,7.33,null,null,7.33,"Leistungsschalter 1000A 3-polig, Micro. 2.0 manuelle Betätigung"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 1250A 3-polig, Micro. 2.0 manuelle Betätigung","PE308S60",null,"Schneider",1250,14.67,null,null,14.67,"Leistungsschalter 1250A 3-polig, Micro. 2.0 manuelle Betätigung"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 1250A 3-polig, Micro. 2.0 Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE308S61",null,"Schneider",160,8.5500000000000007,null,null,8.5500000000000007,"Leistungsschalter 1250A 3-polig, Micro. 2.0 Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 160A 36kA 4-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE402S61",null,"Schneider",160,9.1999999999999993,null,null,9.1999999999999993,"Leistungsschalter 160A 36kA 4-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 250A 36kA 4-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE403S61",null,"Schneider",250,17.600000000000001,null,null,17.600000000000001,"Leistungsschalter 250A 36kA 4-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 400A 50kA 4-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE404S61",null,"Schneider",400,19.2,null,null,19.2,"Leistungsschalter 400A 50kA 4-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 630A 50kA 4-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE405S61",null,"Schneider",630,39.700000000000003,null,null,39.700000000000003,"Leistungsschalter 630A 50kA 4-polig Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 1000A 4-polig, Micro. 2.0 manuelle Betätigung","PE407S60",null,"Schneider",1000,7.3,null,null,7.3,"Leistungsschalter 1000A 4-polig, Micro. 2.0 manuelle Betätigung"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 1000A 4-polig, Micro. 2.0 Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE407S61",null,"Schneider",1000,7.3,null,null,7.3,"Leistungsschalter 1000A 4-polig, Micro. 2.0 Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 1250A 4-polig, Micro. 2.0 manuelle Betätigung","PE408S60",null,"Schneider",1250,14.67,null,null,14.67,"Leistungsschalter 1250A 4-polig, Micro. 2.0 manuelle Betätigung"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 1250A 4-polig, Micro. 2.0 Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE408S61",null,"Schneider",1250,14.67,null,null,14.67,"Leistungsschalter 1250A 4-polig, Micro. 2.0 Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 800A 3-polig 50kA Festeinbau mit Elektrischem Auslößer","XLSS30800E",null,"Schneider",800,5,null,null,5,"Leistungsschalter 800A 3-polig 50kA Festeinbau mit Elektrischem Auslößer"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 250A 4-polig 36KA Festeinbau mit Elektrischem Auslößer","XLSS40250E",null,"Schneider",250,17.600000000000001,null,null,17.600000000000001,"Leistungsschalter 250A 4-polig 36KA Festeinbau mit Elektrischem Auslößer"]
["Leistungsschalter Compact NSX/NS","ComPacT TRIP UNIT NSX160 AC 3P3D 160A 2.2 ","C1632D160",null,"Schneider",160,9.1999999999999993,null,null,{"$f":"G303+I303","v":9.1999999999999993},"ComPacT TRIP UNIT NSX160 AC 3P3D 160A 2.2 "]
["Leistungsschalter Compact NSX/NS","ComPacT TRIP UNIT NSX160 AC 3P3D 125A TMD ","C163TM125",null,"Schneider",125,10.78,null,null,10.78,"ComPacT TRIP UNIT NSX160 AC 3P3D 125A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT TRIP UNIT NSX160 AC 3P3D 160A TMD ","C163TM160",null,"Schneider",160,13.95,null,null,13.95,"ComPacT TRIP UNIT NSX160 AC 3P3D 160A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT TRIP UNIT NSX160 AC 4P4D 160A 2.2 ","C1642D160",null,"Schneider",160,9.1999999999999993,null,null,9.1999999999999993,"ComPacT TRIP UNIT NSX160 AC 4P4D 160A 2.2 "]
["Leistungsschalter Compact NSX/NS","ComPacT TRIP UNIT NSX160 AC 4P3D 125A TMD ","C166TM125",null,"Schneider",125,10.78,null,null,10.78,"ComPacT TRIP UNIT NSX160 AC 4P3D 125A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT TRIP UNIT NSX160 AC 4P3D 160A TMD ","C166TM160",null,"Schneider",160,13.95,null,null,13.95,"ComPacT TRIP UNIT NSX160 AC 4P3D 160A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX160F 36kA AC 4P4D 125A TMD ","C16F4TM125",null,"Schneider",125,10.78,null,null,10.78,"ComPacT BREAKER NSX160F 36kA AC 4P4D 125A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX160N 50kA AC 3P3D 160A TMD ","C16N3TM160",null,"Schneider",160,13.95,null,null,13.95,"ComPacT BREAKER NSX160N 50kA AC 3P3D 160A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250B 25kA AC 3P3D 125A TMD ","C25B3TM125",null,"Schneider",125,9.4499999999999993,null,null,9.4499999999999993,"ComPacT BREAKER NSX250B 25kA AC 3P3D 125A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250B 25kA AC 3P3D 160A TMD ","C25B3TM160",null,"Schneider",160,11.78,null,null,11.78,"ComPacT BREAKER NSX250B 25kA AC 3P3D 160A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250B 25kA AC 3P3D 200A TMD ","C25B3TM200",null,"Schneider",200,15.4,null,null,15.4,"ComPacT BREAKER NSX250B 25kA AC 3P3D 200A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250B 25kA AC 3P3D 250A TMD ","C25B3TM250",null,"Schneider",250,18.75,null,null,18.75,"ComPacT BREAKER NSX250B 25kA AC 3P3D 250A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250F 36kA AC 3P3D 125A TMD ","C25F3TM125",null,"Schneider",125,9.4499999999999993,null,null,9.4499999999999993,"ComPacT BREAKER NSX250F 36kA AC 3P3D 125A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250F 36kA AC 3P3D 160A TMD ","C25F3TM160",null,"Schneider",160,11.78,null,null,11.78,"ComPacT BREAKER NSX250F 36kA AC 3P3D 160A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250F 36kA AC 3P3D 200A TMD ","C25F3TM200",null,"Schneider",200,15.4,null,null,15.4,"ComPacT BREAKER NSX250F 36kA AC 3P3D 200A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250F 36kA AC 4P4D 200A TMD ","C25F4TM200",null,"Schneider",200,15.4,null,null,15.4,"ComPacT BREAKER NSX250F 36kA AC 4P4D 200A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250F 36kA AC 4P4D 250A TMD ","C25F4TM250",null,"Schneider",250,18.75,null,null,18.75,"ComPacT BREAKER NSX250F 36kA AC 4P4D 250A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250H 70kA AC 3P3D 125A TMD ","C25H3TM125",null,"Schneider",125,9.4499999999999993,null,null,9.4499999999999993,"ComPacT BREAKER NSX250H 70kA AC 3P3D 125A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250H 70kA AC 3P3D 160A TMD ","C25H3TM160",null,"Schneider",160,11.78,null,null,11.78,"ComPacT BREAKER NSX250H 70kA AC 3P3D 160A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250H 70kA AC 3P3D 200A TMD ","C25H3TM200",null,"Schneider",200,15.4,null,null,15.4,"ComPacT BREAKER NSX250H 70kA AC 3P3D 200A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250H 70kA AC 3P3D 250A TMD ","C25H3TM250",null,"Schneider",250,18.75,null,null,18.75,"ComPacT BREAKER NSX250H 70kA AC 3P3D 250A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250N 50kA AC 3P3D 125A TMD ","C25N3TM125",null,"Schneider",125,9.4499999999999993,null,null,9.4499999999999993,"ComPacT BREAKER NSX250N 50kA AC 3P3D 125A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250N 50kA AC 3P3D 160A TMD ","C25N3TM160",null,"Schneider",160,11.78,null,null,11.78,"ComPacT BREAKER NSX250N 50kA AC 3P3D 160A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250N 50kA AC 3P3D 200A TMD ","C25N3TM200",null,"Schneider",200,15.4,null,null,15.4,"ComPacT BREAKER NSX250N 50kA AC 3P3D 200A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250N 50kA AC 3P3D 250A TMD ","C25N3TM250",null,"Schneider",250,18.75,null,null,18.75,"ComPacT BREAKER NSX250N 50kA AC 3P3D 250A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250R 200kA AC 3P 125A TMD ","C25R3TM125",null,"Schneider",125,9.4499999999999993,null,null,9.4499999999999993,"ComPacT BREAKER NSX250R 200kA AC 3P 125A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250R 200kA AC 3P 160A TMD ","C25R3TM160",null,"Schneider",160,11.78,null,null,11.78,"ComPacT BREAKER NSX250R 200kA AC 3P 160A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250R 200kA AC 3P 200A TMD ","C25R3TM200",null,"Schneider",200,15.4,null,null,15.4,"ComPacT BREAKER NSX250R 200kA AC 3P 200A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250R 200kA AC 3P 250A TMD ","C25R3TM250",null,"Schneider",250,18.75,null,null,18.75,"ComPacT BREAKER NSX250R 200kA AC 3P 250A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250HB1 75kA AC 3P 125A TMD ","C25V3TM125",null,"Schneider",125,9.4499999999999993,null,null,9.4499999999999993,"ComPacT BREAKER NSX250HB1 75kA AC 3P 125A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250HB1 75kA AC 3P 160A TMD ","C25V3TM160",null,"Schneider",160,11.78,null,null,11.78,"ComPacT BREAKER NSX250HB1 75kA AC 3P 160A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250HB1 75kA AC 3P 200A TMD ","C25V3TM200",null,"Schneider",200,15.4,null,null,15.4,"ComPacT BREAKER NSX250HB1 75kA AC 3P 200A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250HB1 75kA AC 3P 250A TMD ","C25V3TM250",null,"Schneider",250,18.75,null,null,18.75,"ComPacT BREAKER NSX250HB1 75kA AC 3P 250A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250HB2 100kA AC 3P 125A TMD ","C25W3TM125",null,"Schneider",125,9.4499999999999993,null,null,9.4499999999999993,"ComPacT BREAKER NSX250HB2 100kA AC 3P 125A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250HB2 100kA AC 3P 160A TMD ","C25W3TM160",null,"Schneider",160,11.78,null,null,11.78,"ComPacT BREAKER NSX250HB2 100kA AC 3P 160A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250HB2 100kA AC 3P 200A TMD ","C25W3TM200",null,"Schneider",200,15.4,null,null,15.4,"ComPacT BREAKER NSX250HB2 100kA AC 3P 200A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX250HB2 100kA AC 3P 250A TMD ","C25W3TM250",null,"Schneider",250,18.75,null,null,18.75,"ComPacT BREAKER NSX250HB2 100kA AC 3P 250A TMD "]
["Leistungsschalter Compact NSX/NS","Netzumschaltung 250A 4p best. aus 2x LSS mit Motorantrieb und Steuerung","XLSS40250EUM",null,"Schneider",250,17.600000000000001,null,null,17.600000000000001,"Netzumschaltung 250A 4p best. aus 2x LSS mit Motorantrieb und Steuerung"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 800A 3-polig, Micro. 2.0 Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE306S61",null,"Schneider",800,5,null,null,5,"Leistungsschalter 800A 3-polig, Micro. 2.0 Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 1000A 3-polig, Micro. 2.0 Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE307S61",null,"Schneider",1000,7.33,null,null,7.33,"Leistungsschalter 1000A 3-polig, Micro. 2.0 Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 1600A 3-polig, Micro. 2.0 manuelle Betätigung","PE309S60",null,"Schneider",1600,24.67,null,null,24.67,"Leistungsschalter 1600A 3-polig, Micro. 2.0 manuelle Betätigung"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 1600A 3-polig, Micro. 2.0 Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE309S61",null,"Schneider",1600,24.67,null,null,24.67,"Leistungsschalter 1600A 3-polig, Micro. 2.0 Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 800A 4-polig, Micro. 2.0 manuelle Betätigung","PE406S60",null,"Schneider",800,5,null,null,5,"Leistungsschalter 800A 4-polig, Micro. 2.0 manuelle Betätigung"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 800A 4-polig, Micro. 2.0 Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE406S61",null,"Schneider",800,5,null,null,5,"Leistungsschalter 800A 4-polig, Micro. 2.0 Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 1600A 4-polig, Micro. 2.0 manuelle Betätigung","PE409S60",null,"Schneider",1600,24.67,null,null,24.67,"Leistungsschalter 1600A 4-polig, Micro. 2.0 manuelle Betätigung"]
["Leistungsschalter Compact NSX/NS","Leistungsschalter 1600A 4-polig, Micro. 2.0 Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko","PE409S61",null,"Schneider",1600,24.67,null,null,24.67,"Leistungsschalter 1600A 4-polig, Micro. 2.0 Motorantrieb 230VAC + Untersp.sp. 24VDC + 1 Hiko"]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX100F 36kA AC 3P3D 63A TMD ","C10F3TM063",null,"Schneider",63,8.61,null,null,{"$f":"G349+I349","v":8.61},"ComPacT BREAKER NSX100F 36kA AC 3P3D 63A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX100F 36kA AC 4P4D 63A TMD ","C10F4TM063",null,"Schneider",63,8.61,null,null,8.61,"ComPacT BREAKER NSX100F 36kA AC 4P4D 63A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSX100F 36kA AC 4P4D 100A TMD ","C10F4TM100",null,"Schneider",100,8.8000000000000007,null,null,8.8000000000000007,"ComPacT BREAKER NSX100F 36kA AC 4P4D 100A TMD "]
["Leistungsschalter Compact NSX/NS","ComPacT BREAKER NSXm100B 25kA AC 3P 100A TMD ELINK","C11B3TM100L",null,"Schneider",100,8.8000000000000007,null,null,8.8000000000000007,"ComPacT BREAKER NSXm100B 25kA AC 3P 100A TMD ELINK"]
[null,null,null,null,null,null,null,null,null,0]
["SH-Schalter","SH-Schalter",null,null,null,null,null,null,null,0]
["SH-Schalter","SH-Schalter 16A","XHA316-5","3 Pol, SaS Hutschiene","ABN",16,4.0999999999999996,{"$f":"G355*3","v":12.299999999999999},null,4.0999999999999996,"SHU-Schalter 3p 16A Gerätetragschiene-Montage Charakteristik E ABN"]
["SH-Schalter",null,"XHA116-4","1 Pol, SaS Hutschiene","ABN",16,4.0999999999999996,{"$f":"G356","v":4.0999999999999996},null,4.0999999999999996,"SH-Schalter/1-polig/16A Hutschienenmontage_Charakteristik E / ABN"]
["SH-Schalter",null,"XHA116-5",null,"ABN",16,4.0999999999999996,{"$f":"G357","v":4.0999999999999996},null,{"$f":"G357+I357","v":4.0999999999999996},"SHU-Schalter 1p 16A Gerätetragschiene-Montage Charakteristik E ABN"]
["SH-Schalter",null,100038,"3 Pol, SaS 40mm","ABN",16,4.5,{"$f":"G358*3","v":13.5},null,4.5,"SHU-Schalter 3-polig 16A SAS Montage_Charakteristik E / ABN"]
["SH-Schalter",null,"XKS316-5",null,"ABN",16,4.5,{"$f":"G359*3","v":13.5},null,{"$f":"G359+I359","v":4.5},"SHU-Schalter 3p 16A SaS-Montage Charakteristik E ABN"]
["SH-Schalter",null,"XKS116L1-5","1 Pol, SaS 40mm","ABN",16,4.5,{"$f":"G360","v":4.5},null,4.5,"SHU-Schalter 1p 16A SaS-Montage Phase L1 Charakteristik E ABN"]
["SH-Schalter",null,"XKS116L2-5",null,"ABN",16,4.5,{"$f":"G361","v":4.5},null,4.5,"SHU-Schalter 1p 16A SaS-Montage Phase L2 Charakteristik E ABN"]
["SH-Schalter",null,"XKS116L3-5",null,"ABN",16,4.5,{"$f":"G362","v":4.5},null,4.5,"SHU-Schalter 1p 16A SaS-Montage Phase L3 Charakteristik E ABN"]
["SH-Schalter",null,"XKS116-6",null,"ABN",16,4.5,{"$f":"G363","v":4.5},null,4.5,"SH-Schalter für SammelS,1-polig,16A,Typ SHA Charakteristik E , ABN-Logo"]
["SH-Schalter","SH-Schalter 20A","XHA320-5","3 Pol, SaS Hutschiene","ABN",20,5.4,{"$f":"G364*3","v":16.200000000000003},null,5.4,"SHU-Schalter 3p 20A Gerätetragschiene-Montage Charakteristik E ABN"]
["SH-Schalter",null,"XHA120-5","1 Pol, SaS Hutschiene","ABN",20,5.4,{"$f":"G365","v":5.4},null,5.4,"SHU-Schalter 1p 20A Gerätetragschiene-Montage Charakteristik E ABN"]
["SH-Schalter",null,100039,"3 Pol, SaS 40mm","ABN",20,6,{"$f":"G366*3","v":18},null,6,"SHU-Schalter 3-polig 20A SAS Montage_Charakteristik E / ABN"]
["SH-Schalter",null,"XKS320-5",null,"ABN",20,6,{"$f":"G367*3","v":18},null,{"$f":"G367+I367","v":6},"SHU-Schalter 3p 20A SaS-Montage Charakteristik E ABN"]
["SH-Schalter",null,"XKS320-6",null,"ABN",20,6,18,null,6,"SH-Schalter+Adapter/3-polig/20A SammelS-Montage_Charakteristik E / ABN"]
["SH-Schalter",null,"XKS120L1-5","1 Pol, SaS 40mm","ABN",20,6,{"$f":"G369","v":6},null,6,"SHU-Schalter 1p 20A SaS-Montage Phase L1 Charakteristik E ABN"]
["SH-Schalter",null,"XKS120L2-5",null,"ABN",20,6,{"$f":"G370","v":6},null,{"$f":"G370+I370","v":6},"SHU-Schalter 1p 20A SaS-Montage Phase L2 Charakteristik E ABN"]
["SH-Schalter",null,"XKS120L3-5",null,"ABN",20,6,6,null,6,"SHU-Schalter 1p 20A SaS-Montage Phase L3 Charakteristik E ABN"]
["SH-Schalter","SH-Schalter 25A","XHA325-5","3 Pol, SaS Hutschiene","ABN",25,5.9,{"$f":"G372*3","v":17.700000000000003},null,5.9,"SHU-Schalter 3p 25A Gerätetragschiene-Montage Charakteristik E ABN"]
["SH-Schalter",null,"XHA125-5","1 Pol, SaS Hutschiene","ABN",25,5.9,{"$f":"G373","v":5.9},null,5.9,"SHU-Schalter 1p 25A Gerätetragschiene-Montage Charakteristik E ABN"]
["SH-Schalter",null,100040,"3 Pol, SaS 40mm","ABN",25,6.5,{"$f":"G374*3","v":19.5},null,6.5,"SHU-Schalter 3-polig 25A SAS Montage_Charakteristik E / ABN"]
["SH-Schalter",null,"XKS325-5",null,"ABN",25,6.5,{"$f":"G375*3","v":19.5},null,{"$f":"G375+I375","v":6.5},"SHU-Schalter 3p 25A SaS-Montage Charakteristik E ABN"]
["SH-Schalter",null,100023,"1 Pol, SaS 40mm","ABN",25,6.5,{"$f":"G376","v":6.5},null,6.5,"SHU-Schalter 1-polig 25A Phase L1 SAS Montage_Charakteristik E / ABN"]
["SH-Schalter",null,"XKS125L1-5",null,"ABN",25,6.5,{"$f":"G377","v":6.5},null,{"$f":"G377+I377","v":6.5},"SHU-Schalter 1p 25A SaS-Montage Phase L1 Charakteristik E ABN"]
["SH-Schalter",null,"XKS125L2-5",null,"ABN",25,6.5,6.5,null,6.5,"SHU-Schalter 1p 25A SaS-Montage Phase L2 Charakteristik E ABN"]
["SH-Schalter",null,"XKS125L3-5",null,"ABN",25,6.5,6.5,null,6.5,"SHU-Schalter 1p 25A SaS-Montage Phase L3 Charakteristik E ABN"]
["SH-Schalter","SH-Schalter 35A","XHA135-5","3 Pol, SaS Hutschiene","ABN",35,6.3,{"$f":"G380*3","v":18.899999999999999},null,6.3,"SHU-Schalter 1p 35A Gerätetragschiene-Montage Charakteristik E ABN"]
["SH-Schalter",null,100012,"1 Pol, SaS Hutschiene","ABN",35,6.3,{"$f":"G381","v":6.3},null,6.3,"SHU-Schalter 3-polig 35A Hutschienenmontage_Charakteristik E / ABN"]
["SH-Schalter",null,"XHA335-5",null,"ABN",35,6.3,{"$f":"G382","v":6.3},null,{"$f":"G382+I382","v":6.3},"SHU-Schalter 3p 35A Gerätetragschiene-Montage Charakteristik E ABN"]
["SH-Schalter",null,100041,"3 Pol, SaS 40mm","ABN",35,6.9,{"$f":"G383*3","v":20.700000000000003},null,6.9,"SHU-Schalter 3-polig 35A SAS Montage_Charakteristik E / ABN"]
["SH-Schalter",null,"XKS335-5",null,"ABN",35,6.9,{"$f":"G384*3","v":20.700000000000003},null,{"$f":"G384+I384","v":6.9},"SHU-Schalter 3p 35A SaS-Montage Charakteristik E ABN"]
["SH-Schalter",null,"XKS135L1-5","1 Pol, SaS 40mm","ABN",35,6.9,{"$f":"G385","v":6.9},null,6.9,"SHU-Schalter 1p 35A SaS-Montage Phase L1 Charakteristik E ABN"]
["SH-Schalter",null,"XKS135L2-5",null,"ABN",35,6.9,6.9,null,6.9,"SHU-Schalter 1p 35A SaS-Montage Phase L2 Charakteristik E ABN"]
["SH-Schalter",null,"XKS135L3-5",null,"ABN",35,6.9,6.9,null,6.9,"SHU-Schalter 1p 35A SaS-Montage Phase L3 Charakteristik E ABN"]
["SH-Schalter",null,100026,null,"ABN",35,6.9,{"$f":"G388","v":6.9},null,6.9,"SHU-Schalter 1-polig 35A Phase L1 SAS Montage_Charakteristik E / ABN"]
["SH-Schalter","SH-Schalter 40A",100013,"3 Pol, SaS Hutschiene","ABN",40,6.1,{"$f":"G389*3","v":18.299999999999997},null,6.1,"SHU-Schalter 3-polig 40A Hutschienenmontage_Charakteristik E / ABN"]
["SH-Schalter",null,"XHA340-5",null,"ABN",40,6.1,{"$f":"G390*3","v":18.299999999999997},null,{"$f":"G390+I390","v":6.1},"SHU-Schalter 3p 40A Gerätetragschiene-Montage Charakteristik E ABN"]
["SH-Schalter",null,"XHA140-5","1 Pol, SaS Hutschiene","ABN",40,6.1,{"$f":"G391","v":6.1},null,6.1,"SHU-Schalter 1p 40A Gerätetragschiene-Montage Charakteristik E ABN"]
["SH-Schalter",null,"XKS340-5","3 Pol, SaS 40mm","ABN",40,6.4,{"$f":"G392*3","v":19.200000000000003},null,6.4,"SHU-Schalter 3p 40A SaS-Montage Charakteristik E ABN"]
["SH-Schalter",null,"XKS140L1-5","1 Pol, SaS 40mm","ABN",40,6.4,{"$f":"G393","v":6.4},null,{"$f":"G393+I393","v":6.4},"SHU-Schalter 1p 40A SaS-Montage Phase L1 Charakteristik E ABN"]
["SH-Schalter",null,"XKS140L2-5",null,"ABN",40,6.4,6.4,null,6.4,"SHU-Schalter 1p 40A SaS-Montage Phase L2 Charakteristik E ABN"]
["SH-Schalter",null,"XKS140L3-5",null,"ABN",40,6.4,{"$f":"G395","v":6.4},null,6.4,"SHU-Schalter 1p 40A SaS-Montage Phase L3 Charakteristik E ABN"]
["SH-Schalter","SH-Schalter 50A",100014,"3 Pol, SaS Hutschiene","ABN",50,7.6,{"$f":"G396*3","v":22.799999999999997},null,7.6,"SHU-Schalter 3-polig 50A Hutschienenmontage_Charakteristik E / ABN"]
["SH-Schalter",null,"XHA350-5",null,"ABN",50,7.6,{"$f":"G397*3","v":22.799999999999997},null,{"$f":"G397+I397","v":7.6},"SHU-Schalter 3p 50A Gerätetragschiene-Montage Charakteristik E ABN"]
["SH-Schalter",null,"XHA150-5","1 Pol, SaS Hutschiene","ABN",50,7.6,{"$f":"G398","v":7.6},null,7.6,"SHU-Schalter 1p 50A Gerätetragschiene-Montage Charakteristik E ABN"]
["SH-Schalter",null,100043,"3 Pol, SaS 40mm","ABN",50,8,{"$f":"G399*3","v":24},null,8,"SHU-Schalter 3-polig 50A SAS Montage_Charakteristik E / ABN"]
["SH-Schalter",null,"XKS350-5",null,"ABN",50,8,{"$f":"G400*3","v":24},null,{"$f":"G400+I400","v":8},"SHU-Schalter 3p 50A SaS-Montage Charakteristik E ABN"]
["SH-Schalter",null,"XKS150L1-5","1 Pol, SaS 40mm","ABN",50,8,{"$f":"G401","v":8},null,8,"SHU-Schalter 1p 50A SaS-Montage Phase L1 Charakteristik E ABN"]
["SH-Schalter",null,"XKS150L2-5",null,"ABN",50,8,8,null,8,"SHU-Schalter 1p 50A SaS-Montage Phase L2 Charakteristik E ABN"]
["SH-Schalter",null,"XKS150L3-5",null,"ABN",50,8,{"$f":"G403","v":8},null,8,"SHU-Schalter 1p 50A SaS-Montage Phase L3 Charakteristik E ABN"]
["SH-Schalter","SH-Schalter 63A",100015,"3 Pol, SaS Hutschiene","ABN",63,8.6999999999999993,{"$f":"G404*3","v":26.099999999999998},null,8.6999999999999993,"SHU-Schalter 3-polig 63A Hutschienenmontage_Charakteristik E / ABN"]
["SH-Schalter",null,"XHA363-5",null,"ABN",63,8.6999999999999993,{"$f":"G405*3","v":26.099999999999998},null,{"$f":"G405+I405","v":8.6999999999999993},"SHU-Schalter 3p 63A Gerätetragschiene-Montage Charakteristik E ABN"]
["SH-Schalter",null,"XHA163-5","1 Pol, SaS Hutschiene","ABN",63,8.6999999999999993,{"$f":"G406","v":8.6999999999999993},null,8.6999999999999993,"SHU-Schalter 1p 63A Gerätetragschiene-Montage Charakteristik E ABN"]
["SH-Schalter",null,100044,"3 Pol, SaS 40mm","ABN",63,9.6999999999999993,{"$f":"G407*3","v":29.099999999999998},null,9.6999999999999993,"SHU-Schalter 3-polig 63A SAS Montage_Charakteristik E / ABN"]
["SH-Schalter",null,"XKS363-5",null,"ABN",63,9.6999999999999993,{"$f":"G408*3","v":29.099999999999998},null,{"$f":"G408+I408","v":9.6999999999999993},"SHU-Schalter 3p 63A SaS-Montage Charakteristik E ABN"]
["SH-Schalter",null,"XKS163L1-5","1 Pol, SaS 40mm","ABN",63,9.6999999999999993,{"$f":"G409","v":9.6999999999999993},null,9.6999999999999993,"SHU-Schalter 1p 63A SaS-Montage Phase L1 Charakteristik E ABN"]
["SH-Schalter",null,"XKS163L2-5",null,"ABN",null,9.6999999999999993,9.6999999999999993,null,9.6999999999999993,"SHU-Schalter 1p 63A SaS-Montage Phase L2 Charakteristik E ABN"]
["SH-Schalter",null,"XKS163L3-5",null,"ABN",null,9.6999999999999993,{"$f":"G411","v":9.6999999999999993},null,{"$f":"G411+I411","v":9.6999999999999993},"SHU-Schalter 1p 63A SaS-Montage Phase L3 Charakteristik E ABN"]
["SH-Schalter","SH-Schalter 80A",100181,"3 Pol, SaS Hutschiene","ABN",80,10.5,{"$f":"G412*3","v":31.5},null,10.5,"SH-Schalter 3-polig, 80A, 25kA Charakteristik E für Hutschienenmontage"]
["SH-Schalter",null,100829,null,"ABN",80,10.5,{"$f":"G413*3","v":31.5},null,{"$f":"G413+I413","v":10.5},"SHU-Schalter/3-polig/80A  Hutschienenmontage Charakteristik E/ABB"]
["SH-Schalter",null,"XHA380-5",null,"ABN",80,10.5,31.5,null,10.5,"SHU-Schalter/3-polig/80A  Hutschienenmontage Charakteristik E/ABB"]
["SH-Schalter",null,"XHA180-2","1 Pol, SaS Hutschiene","ABN",80,10.5,{"$f":"G415","v":10.5},null,10.5,"SH-Schalter 1p 80A Gerätetragschiene-Montage Charakteristik E ABB"]
["SH-Schalter","SH-Schalter 100A",100163,"3 Pol, SaS 40mm","ABN",100,12,{"$f":"G416*3","v":36},null,12,"SH-Schalter 3-polig, 100A, 25kA Charakteristik E für Hutschienenmontage"]
["SH-Schalter",null,"XHA399-5",null,"ABN",100,12,{"$f":"G417*3","v":36},null,{"$f":"G417+I417","v":12},"SHU-Schalter 3p 100A Gerätetragschiene-Montage Charakteristik E/ABB"]
["SH-Schalter",null,"XHA199-2","1 Pol, SaS 40mm","ABN",100,12,{"$f":"G418","v":12},null,12,"SH-Schalter 1p 100A Gerätetragschiene-Montage Charakteristik E ABB"]
["SH-Schalter",null,"XKS399-2","3 Pol, SaS Hutschiene","ABN",100,14.4,{"$f":"G419*3","v":43.2},null,14.4,"SH-Schalter+Adapter/3-polig/100A  SaS-Montage Charakteristik E/ABB"]
["SH-Schalter","SaS Quickadapter für SH-Schalter 3-polig 80/100A",100164,"SaS-Adapter für XHA","ABN",100,{"$f":"H420/3","v":3},9,null,3,"SaS Quickadapter für SH-Schalter 3-polig 80/100A"]
[null,null,null,null,null,null,null,null,null,0]
["Hauptschalter","Hauptschalter",null,null,null,null,null,null,null,0]
["Hauptschalter","Hauptschalter 63A","XHS363",null,"ABN",63,4.8,{"$f":"G423*3","v":14.399999999999999},null,4.8,"Hauptschalter 3p 63A 3TE 10kA"]
["Hauptschalter",null,"XHS463",null,"ABN",63,4.8,{"$f":"G424*3","v":14.399999999999999},null,{"$f":"G424+I424","v":4.8},"Hauptschalter 4p 63A 4TE 10kA"]
["Hauptschalter",null,"XHS363-1",null,"ABN",63,{"$f":"H425/3","v":1.8},5.4,null,1.8,"Hauptschalter 3p 63A verriegelbar 2.5TE 10kA"]
["Hauptschalter","Hauptschalter 100A","XHS399",null,"ABN",100,3.87,{"$f":"G426*3","v":11.61},null,3.87,"Hauptschalter 3p 100A 3TE 10kA"]
[null,null,null,null,null,null,null,null,null,0]
[null,null,null,null,null,null,null,null,null,0]
["FI/LS-Schalter","FI/LS 1P+N","Acti9","10kA","Schneider",null,null,null,null,0,"FI/LS 1P+N"]
["FI/LS-Schalter","FI/LS iDPN H Vigi, 1P+N, 6A, B-Char., 30mA, Typ A","A9D07606","10kA","Schneider",6,2.7,2.7,null,2.7,"FI/LS iDPN H Vigi, 1P+N, 6A, B-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN H Vigi, 1P+N, 10A, B-Char., 30mA, Typ A","A9D07610","10kA","Schneider",10,2.7,2.7,null,2.7,"FI/LS iDPN H Vigi, 1P+N, 10A, B-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN H Vigi, 1P+N, 16A, B-Char., 30mA, Typ A","A9D07616","10kA","Schneider",16,3.2,3.2,null,3.2,"FI/LS iDPN H Vigi, 1P+N, 16A, B-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN H Vigi, 1P+N, 20A, B-Char., 30mA, Typ A","A9D07620","10kA","Schneider",20,4.7,4.7,null,4.7,"FI/LS iDPN H Vigi, 1P+N, 20A, B-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN H Vigi, 1P+N, 25A, B-Char., 30mA, Typ A","A9D07625","10kA","Schneider",25,4.7,4.7,null,4.7,"FI/LS iDPN H Vigi, 1P+N, 25A, B-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN H Vigi, 1P+N, 32A, B-Char., 30mA, Typ A","A9D07632","10kA","Schneider",32,4.5999999999999996,4.5999999999999996,null,4.5999999999999996,"FI/LS iDPN H Vigi, 1P+N, 32A, B-Char., 30mA, Typ A"]
["FI/LS-Schalter",null,null,null,null,null,null,null,null,0]
["FI/LS-Schalter","FI/LS iDPN H Vigi, 1P+N, 10A, B-Char., 10mA, Typ A","A9D08610","10kA","Schneider",10,2.7,2.7,null,2.7,"FI/LS iDPN H Vigi, 1P+N, 10A, B-Char., 10mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN H Vigi, 1P+N, 16A, B-Char., 10mA, Typ A","A9D08616","10kA","Schneider",16,3.2,3.2,null,3.2,"FI/LS iDPN H Vigi, 1P+N, 16A, B-Char., 10mA, Typ A"]
["FI/LS-Schalter",null,null,null,null,null,null,null,null,0]
["FI/LS-Schalter","FI/LS 1P+N","Acti9","10kA","Schneider",null,null,null,null,0,"FI/LS 1P+N"]
["FI/LS-Schalter","FI/LS iDPN H Vigi, 1P+N, 6A, C-Char., 30mA, Typ A","A9D32606","10kA","Schneider",6,2.7,2.7,null,2.7,"FI/LS iDPN H Vigi, 1P+N, 6A, C-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN H Vigi, 1P+N, 10A, C-Char., 30mA, Typ A","A9D32610","10kA","Schneider",10,2.7,2.7,null,2.7,"FI/LS iDPN H Vigi, 1P+N, 10A, C-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN H Vigi, 1P+N, 13A, C-Char., 30mA, Typ A","A9D32613","10kA","Schneider",13,3.3,3.3,null,3.3,"FI/LS iDPN H Vigi, 1P+N, 13A, C-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN H Vigi, 1P+N, 16A, C-Char., 30mA, Typ A","A9D32616","10kA","Schneider",16,3.2,3.2,null,3.2,"FI/LS iDPN H Vigi, 1P+N, 16A, C-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN H Vigi, 1P+N, 20A, C-Char., 30mA, Typ A","A9D32620","10kA","Schneider",20,4.7,4.7,null,4.7,"FI/LS iDPN H Vigi, 1P+N, 20A, C-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN H Vigi, 1P+N, 25A, C-Char., 30mA, Typ A","A9D32625","10kA","Schneider",25,4.7,4.7,null,4.7,"FI/LS iDPN H Vigi, 1P+N, 25A, C-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN H Vigi, 1P+N, 32A, C-Char., 30mA, Typ A","A9D32632","10kA","Schneider",32,4.5999999999999996,4.5999999999999996,null,4.5999999999999996,"FI/LS iDPN H Vigi, 1P+N, 32A, C-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN H Vigi, 1P+N, 40A, C-Char., 30mA, Typ A","A9D32640","10kA","Schneider",40,5.8,5.8,null,5.8,"FI/LS iDPN H Vigi, 1P+N, 40A, C-Char., 30mA, Typ A"]
["FI/LS-Schalter",null,null,null,null,null,null,null,null,0]
["FI/LS-Schalter","FI/LS 1P+N","Acti9","6kA","Schneider",null,null,null,null,0,"FI/LS 1P+N"]
["FI/LS-Schalter","FI/LS iDPN N Vigi, 1P+N, 6A, B-Char., 30mA, Typ A","A9D56606","6kA","Schneider",6,2.7,2.7,null,2.7,"FI/LS iDPN N Vigi, 1P+N, 6A, B-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN N Vigi, 1P+N, 10A, B-Char., 30mA, Typ A","A9D56610","6kA","Schneider",10,2.7,2.7,null,2.7,"FI/LS iDPN N Vigi, 1P+N, 10A, B-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN N Vigi, 1P+N, 13A, B-Char., 30mA, Typ A","A9D56613","6kA","Schneider",13,3.3,3.3,null,3.3,"FI/LS iDPN N Vigi, 1P+N, 13A, B-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN N Vigi, 1P+N, 16A, B-Char., 30mA, Typ A","A9D56616","6kA","Schneider",16,3.2,3.2,null,3.2,"FI/LS iDPN N Vigi, 1P+N, 16A, B-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN N Vigi, 1P+N, 20A, B-Char., 30mA, Typ A","A9D56620","6kA","Schneider",20,4.7,4.7,null,4.7,"FI/LS iDPN N Vigi, 1P+N, 20A, B-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN N Vigi, 1P+N, 25A, B-Char., 30mA, Typ A","A9D56625","6kA","Schneider",25,4.7,4.7,null,4.7,"FI/LS iDPN N Vigi, 1P+N, 25A, B-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN N Vigi, 1P+N, 32A, B-Char., 30mA, Typ A","A9D56632","6kA","Schneider",32,4.5999999999999996,4.5999999999999996,null,4.5999999999999996,"FI/LS iDPN N Vigi, 1P+N, 32A, B-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN N Vigi, 1P+N, 40A, B-Char., 30mA, Typ A","A9D56640","6kA","Schneider",40,5.8,5.8,null,5.8,"FI/LS iDPN N Vigi, 1P+N, 40A, B-Char., 30mA, Typ A"]
["FI/LS-Schalter",null,null,null,null,null,null,null,null,0]
["FI/LS-Schalter","FI/LS 1P+N","Acti9","6kA","Schneider",null,null,null,null,0,"FI/LS 1P+N"]
["FI/LS-Schalter","FI/LS iDPN N Vigi, 1P+N, 6A, B-Char., 100mA, Typ A","A9D60606","6kA","Schneider",6,2.7,2.7,null,2.7,"FI/LS iDPN N Vigi, 1P+N, 6A, B-Char., 100mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN N Vigi, 1P+N, 10A, B-Char., 100mA, Typ A","A9D60610","6kA","Schneider",10,2.7,2.7,null,2.7,"FI/LS iDPN N Vigi, 1P+N, 10A, B-Char., 100mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN N Vigi, 1P+N, 13A, B-Char., 100mA, Typ A","A9D60613","6kA","Schneider",13,3.3,3.3,null,3.3,"FI/LS iDPN N Vigi, 1P+N, 13A, B-Char., 100mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN N Vigi, 1P+N, 16A, B-Char., 100mA, Typ A","A9D60616","6kA","Schneider",16,3.2,3.2,null,3.2,"FI/LS iDPN N Vigi, 1P+N, 16A, B-Char., 100mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN N Vigi, 1P+N, 20A, B-Char., 100mA, Typ A","A9D60620","6kA","Schneider",20,4.7,4.7,null,4.7,"FI/LS iDPN N Vigi, 1P+N, 20A, B-Char., 100mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN N Vigi, 1P+N, 25A, B-Char., 100mA, Typ A","A9D60625","6kA","Schneider",25,4.7,4.7,null,4.7,"FI/LS iDPN N Vigi, 1P+N, 25A, B-Char., 100mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN N Vigi, 1P+N, 32A, B-Char., 100mA, Typ A","A9D60632","6kA","Schneider",32,4.5999999999999996,4.5999999999999996,null,4.5999999999999996,"FI/LS iDPN N Vigi, 1P+N, 32A, B-Char., 100mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN N Vigi, 1P+N, 40A, B-Char., 100mA, Typ A","A9D60640","6kA","Schneider",40,5.8,5.8,null,5.8,"FI/LS iDPN N Vigi, 1P+N, 40A, B-Char., 100mA, Typ A"]
["FI/LS-Schalter",null,null,null,null,null,null,null,null,0]
["FI/LS-Schalter","FI/LS 1P+N","Acti9","6kA","Schneider",null,null,null,null,0,"FI/LS 1P+N"]
["FI/LS-Schalter","FI/LS iDPN N Vigi, 1P+N, 6A, B-Char., 300mA, Typ A","A9D69606","6kA","Schneider",6,2.7,2.7,null,2.7,"FI/LS iDPN N Vigi, 1P+N, 6A, B-Char., 300mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN N Vigi, 1P+N, 10A, B-Char., 300mA, Typ A","A9D69610","6kA","Schneider",10,2.7,2.7,null,2.7,"FI/LS iDPN N Vigi, 1P+N, 10A, B-Char., 300mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN N Vigi, 1P+N, 13A, B-Char., 300mA, Typ A","A9D69613","6kA","Schneider",13,3.3,3.3,null,3.3,"FI/LS iDPN N Vigi, 1P+N, 13A, B-Char., 300mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN N Vigi, 1P+N, 16A, B-Char., 300mA, Typ A","A9D69616","6kA","Schneider",16,3.2,3.2,null,3.2,"FI/LS iDPN N Vigi, 1P+N, 16A, B-Char., 300mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN N Vigi, 1P+N, 20A, B-Char., 300mA, Typ A","A9D69620","6kA","Schneider",20,4.7,4.7,null,4.7,"FI/LS iDPN N Vigi, 1P+N, 20A, B-Char., 300mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN N Vigi, 1P+N, 25A, B-Char., 300mA, Typ A","A9D69625","6kA","Schneider",25,4.7,4.7,null,4.7,"FI/LS iDPN N Vigi, 1P+N, 25A, B-Char., 300mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN N Vigi, 1P+N, 32A, B-Char., 300mA, Typ A","A9D69632","6kA","Schneider",32,4.5999999999999996,4.5999999999999996,null,4.5999999999999996,"FI/LS iDPN N Vigi, 1P+N, 32A, B-Char., 300mA, Typ A"]
["FI/LS-Schalter","FI/LS iDPN N Vigi, 1P+N, 40A, B-Char., 300mA, Typ A","A9D69640","6kA","Schneider",40,5.8,5.8,null,{"$f":"G478+I478","v":5.8},"FI/LS iDPN N Vigi, 1P+N, 40A, B-Char., 300mA, Typ A"]
["FI/LS-Schalter",null,null,null,null,null,null,null,null,0]
["FI/LS-Schalter","FI/LS 3P","Acti9","6kA","Schneider",null,null,null,null,0,"FI/LS 3P"]
["FI/LS-Schalter","FI/LS iC60N, 3P, 10A, C-Char., 30mA, Typ A","A9D67310","6kA","Schneider",10,3.2,{"$f":"G481*3","v":9.6000000000000014},null,3.2,"FI/LS iC60N, 3P, 10A, C-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iC60N, 3P, 16A, C-Char., 30mA, Typ A","A9D67316","6kA","Schneider",16,4.9000000000000004,{"$f":"G482*3","v":14.700000000000001},null,4.9000000000000004,"FI/LS iC60N, 3P, 16A, C-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iC60N, 3P, 20A, C-Char., 30mA, Typ A","A9D67320","6kA","Schneider",20,6.8,20.399999999999999,null,6.8,"FI/LS iC60N, 3P, 20A, C-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iC60N, 3P, 25A, C-Char., 30mA, Typ A","A9D67325","6kA","Schneider",25,7.6,22.799999999999997,null,7.6,"FI/LS iC60N, 3P, 25A, C-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iC60N, 3P, 32A, C-Char., 30mA, Typ A","A9D67332","6kA","Schneider",32,9.3000000000000007,27.900000000000002,null,9.3000000000000007,"FI/LS iC60N, 3P, 32A, C-Char., 30mA, Typ A"]
["FI/LS-Schalter",null,null,null,null,null,null,null,null,0]
["FI/LS-Schalter","FI/LS 4P","Acti9","6kA","Schneider",null,null,null,null,0,"FI/LS 4P"]
["FI/LS-Schalter","FI/LS iC60N, 4P, 10A, B-Char., 30mA, Typ A","A9D87410","6kA","Schneider",10,3.2,{"$f":"G488*3","v":9.6000000000000014},null,3.2,"FI/LS iC60N, 4P, 10A, B-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iC60N, 4P, 16A, B-Char., 30mA, Typ A","A9D87416","6kA","Schneider",16,4.9000000000000004,{"$f":"G489*3","v":14.700000000000001},null,4.9000000000000004,"FI/LS iC60N, 4P, 16A, B-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iC60N, 4P, 20A, B-Char., 30mA, Typ A","A9D87420","6kA","Schneider",20,6.8,20.399999999999999,null,6.8,"FI/LS iC60N, 4P, 20A, B-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iC60N, 4P, 25A, B-Char., 30mA, Typ A","A9D87425","6kA","Schneider",25,7.6,22.799999999999997,null,7.6,"FI/LS iC60N, 4P, 25A, B-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iC60N, 4P, 32A, B-Char., 30mA, Typ A","A9D87432","6kA","Schneider",32,9.3000000000000007,27.900000000000002,null,9.3000000000000007,"FI/LS iC60N, 4P, 32A, B-Char., 30mA, Typ A"]
["FI/LS-Schalter",null,null,null,null,null,null,null,null,0]
["FI/LS-Schalter","FI/LS 4P","Acti9","6kA","Schneider",null,null,null,null,0,"FI/LS 4P"]
["FI/LS-Schalter","FI/LS iC60N, 4P, 10A, C-Char., 30mA, Typ A","A9D67410","6kA","Schneider",10,3.2,{"$f":"G495*3","v":9.6000000000000014},null,3.2,"FI/LS iC60N, 4P, 10A, C-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iC60N, 4P, 16A, C-Char., 30mA, Typ A","A9D67416","6kA","Schneider",16,4.9000000000000004,{"$f":"G496*3","v":14.700000000000001},null,4.9000000000000004,"FI/LS iC60N, 4P, 16A, C-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iC60N, 4P, 20A, C-Char., 30mA, Typ A","A9D67420","6kA","Schneider",20,6.8,20.399999999999999,null,6.8,"FI/LS iC60N, 4P, 20A, C-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iC60N, 4P, 25A, C-Char., 30mA, Typ A","A9D67425","6kA","Schneider",25,7.6,22.799999999999997,null,7.6,"FI/LS iC60N, 4P, 25A, C-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iC60N, 4P, 32A, C-Char., 30mA, Typ A","A9D67432","6kA","Schneider",32,9.3000000000000007,27.900000000000002,null,9.3000000000000007,"FI/LS iC60N, 4P, 32A, C-Char., 30mA, Typ A"]
["FI/LS-Schalter",null,null,null,null,null,null,null,null,0]
["FI/LS-Schalter","FI/LS 2P","Acti9","10kA","Schneider",null,null,null,null,0,"FI/LS 2P"]
["FI/LS-Schalter","FI/LS iC60H, 2P, 10A, B-Char., 30mA, Typ A","A9D37210","10kA","Schneider",10,3.2,{"$f":"G502*2","v":6.4},null,3.2,"FI/LS iC60H, 2P, 10A, B-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iC60H, 2P, 16A, B-Char., 30mA, Typ A","A9D37216","10kA","Schneider",16,4.9000000000000004,{"$f":"G503*2","v":9.8000000000000007},null,4.9000000000000004,"FI/LS iC60H, 2P, 16A, B-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iC60H, 2P, 20A, B-Char., 30mA, Typ A","A9D37220","10kA","Schneider",20,6.8,13.6,null,6.8,"FI/LS iC60H, 2P, 20A, B-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LS iC60H, 2P, 25A, B-Char., 30mA, Typ A","A9D37225","10kA","Schneider",25,7.6,15.2,null,7.6,"FI/LS iC60H, 2P, 25A, B-Char., 30mA, Typ A"]
["FI/LS-Schalter","FI/LSiC60H, 2P, 32A, B-Char., 30mA, Typ A","A9D37232","10kA","Schneider",32,9.3000000000000007,18.600000000000001,null,9.3000000000000007,"FI/LSiC60H, 2P, 32A, B-Char., 30mA, Typ A"]
["FI/LS-Schalter",null,null,null,null,null,null,null,null,0]
["FI/LS-Schalter","FI/LS 2P","Acti9","10kA","Schneider",null,null,null,null,0,"FI/LS 2P"]
["FI/LS-Schalter","FI/LS iC60H, 2P, 10A, B-Char., 30mA, Typ A SI","A9D47210","10kA","Schneider",10,3.2,{"$f":"G509*2","v":6.4},null,3.2,"FI/LS iC60H, 2P, 10A, B-Char., 30mA, Typ A SI"]
["FI/LS-Schalter","FI/LS iC60H, 2P, 16A, B-Char., 30mA, Typ A SI","A9D47216","10kA","Schneider",16,4.9000000000000004,{"$f":"G510*2","v":9.8000000000000007},null,4.9000000000000004,"FI/LS iC60H, 2P, 16A, B-Char., 30mA, Typ A SI"]
["FI/LS-Schalter","FI/LS iC60H, 2P, 20A, B-Char., 30mA, Typ A SI","A9D47220","10kA","Schneider",20,6.8,13.6,null,6.8,"FI/LS iC60H, 2P, 20A, B-Char., 30mA, Typ A SI"]
["FI/LS-Schalter","FI/LS iC60H, 2P, 25A, B-Char., 30mA, Typ A SI","A9D47225","10kA","Schneider",25,7.6,15.2,null,7.6,"FI/LS iC60H, 2P, 25A, B-Char., 30mA, Typ A SI"]
["FI/LS-Schalter","FI/LSiC60H, 2P, 32A, B-Char., 30mA, Typ A SI","A9D47232","10kA","Schneider",32,9.3000000000000007,18.600000000000001,null,9.3000000000000007,"FI/LSiC60H, 2P, 32A, B-Char., 30mA, Typ A SI"]
["FI/LS-Schalter",null,null,null,null,null,null,null,null,0]
["FI/LS-Schalter","FI/LS 2P","Acti9","10kA","Schneider",null,null,null,null,0,"FI/LS 2P"]
["FI/LS-Schalter","FI/LS iC60H, 2P, 10A, C-Char., 300mA, Typ A SI","A9D54210","10kA","Schneider",10,3.2,{"$f":"G516*2","v":6.4},null,3.2,"FI/LS iC60H, 2P, 10A, C-Char., 300mA, Typ A SI"]
["FI/LS-Schalter","FI/LS iC60H, 2P, 16A, C-Char., 300mA, Typ A SI","A9D54216","10kA","Schneider",16,4.9000000000000004,{"$f":"G517*2","v":9.8000000000000007},null,4.9000000000000004,"FI/LS iC60H, 2P, 16A, C-Char., 300mA, Typ A SI"]
["FI/LS-Schalter","FI/LS iC60H, 2P, 20A, C-Char., 300mA, Typ A SI","A9D54220","10kA","Schneider",20,6.8,13.6,null,6.8,"FI/LS iC60H, 2P, 20A, C-Char., 300mA, Typ A SI"]
["FI/LS-Schalter","FI/LS iC60H, 2P, 25A, C-Char., 300mA, Typ A SI","A9D54225","10kA","Schneider",25,7.6,15.2,null,7.6,"FI/LS iC60H, 2P, 25A, C-Char., 300mA, Typ A SI"]
["FI/LS-Schalter","FI/LSiC60H, 2P, 32A, C-Char., 300mA, Typ A SI","A9D54232","10kA","Schneider",32,9.3000000000000007,18.600000000000001,null,9.3000000000000007,"FI/LSiC60H, 2P, 32A, C-Char., 300mA, Typ A SI"]
["FI/LS-Schalter",null,null,null,null,null,null,null,null,0]
["FI/LS-Schalter","FI/LS 3P","Acti9","10kA","Schneider",null,null,null,null,0,"FI/LS 3P"]
["FI/LS-Schalter","FI/LS iC60H,3P, 10A, C-Char., 30mA, Typ A SI","A9D17310","10kA","Schneider",10,3.2,{"$f":"G523*3","v":9.6000000000000014},null,3.2,"FI/LS iC60H,3P, 10A, C-Char., 30mA, Typ A SI"]
["FI/LS-Schalter","FI/LS iC60H, 3P, 16A, C-Char., 30mA, Typ A SI","A9D17316","10kA","Schneider",16,4.9000000000000004,{"$f":"G524*3","v":14.700000000000001},null,4.9000000000000004,"FI/LS iC60H, 3P, 16A, C-Char., 30mA, Typ A SI"]
["FI/LS-Schalter","FI/LS iC60H, 3P, 20A, C-Char., 30mA, Typ A SI","A9D17320","10kA","Schneider",20,6.8,20.399999999999999,null,6.8,"FI/LS iC60H, 3P, 20A, C-Char., 30mA, Typ A SI"]
["FI/LS-Schalter","FI/LS iC60H, 3P, 25A, C-Char., 30mA, Typ A SI","A9D17325","10kA","Schneider",25,7.6,22.799999999999997,null,7.6,"FI/LS iC60H, 3P, 25A, C-Char., 30mA, Typ A SI"]
["FI/LS-Schalter","FI/LSiC60H, 3P, 32A, C-Char., 30mA, Typ A SI","A9D17332","10kA","Schneider",32,9.3000000000000007,27.900000000000002,null,9.3000000000000007,"FI/LSiC60H, 3P, 32A, C-Char., 30mA, Typ A SI"]
["FI/LS-Schalter"]
["FI/LS-Schalter","FI/LS-Schalter 2P, 16A, C-Char., 30mA, Typ A, 10kA iC60H","A9D17216","10kA","Schneider",16,4.9000000000000004,null,null,{"$f":"G529+I529","v":4.9000000000000004},"FI/LS-Schalter 2P, 16A, C-Char., 30mA, Typ A, 10kA iC60H"]
["FI/LS-Schalter","FI/LS-Schalter iDPN H Vigi, 1p+N, 16A, 30mA Typ A C-Char., 10kA","A9D37616","10kA","Schneider",16,3.2,null,null,3.2,"FI/LS-Schalter iDPN H Vigi, 1p+N, 16A, 30mA Typ A C-Char., 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN H Vigi, 1p+N, 25A, 30mA Typ A C-Char., 10kA","A9D37625","10kA","Schneider",25,4.0999999999999996,null,null,4.0999999999999996,"FI/LS-Schalter iDPN H Vigi, 1p+N, 25A, 30mA Typ A C-Char., 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 4A, 30mA Typ A B-Char., 6kA","A9D56604","6kA","Schneider",4,1.5,null,null,1.5,"FI/LS-Schalter iDPN N Vigi, 1p+N, 4A, 30mA Typ A B-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60N, 4P, 16A, B-Char., 30mA Typ A SI, 6kA","A9D97416","6kA","Schneider",16,4.9000000000000004,null,null,4.9000000000000004,"FI/LS-Schalter iC60N, 4P, 16A, B-Char., 30mA Typ A SI, 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60N, 4P, 32A, B-Char., 30mA Typ A SI, 6kA","A9D97432","6kA","Schneider",32,9.3000000000000007,null,null,9.3000000000000007,"FI/LS-Schalter iC60N, 4P, 32A, B-Char., 30mA Typ A SI, 6kA"]
["FI/LS-Schalter","FI/LS-Schalter Resi9 1P+N, 16A, B-Char. 30mA, Typ A, 6kA","R9D01616","6kA","Schneider",16,4.3,null,null,4.3,"FI/LS-Schalter Resi9 1P+N, 16A, B-Char. 30mA, Typ A, 6kA"]
["FI/LS-Schalter","FI/LS-Schalter Resi9 1P+N, 16A, B-Char. 30mA, Typ A, 10kA","R9D02616","10kA","Schneider",16,3.2,null,null,3.2,"FI/LS-Schalter Resi9 1P+N, 16A, B-Char. 30mA, Typ A, 10kA"]
["FI/LS-Schalter","FI/LS-Schalter Resi9 1P+N, 16A, B-Char. 30mA, Typ F, 6kA","R9D41616","6kA","Schneider",16,3.2,null,null,3.2,"FI/LS-Schalter Resi9 1P+N, 16A, B-Char. 30mA, Typ F, 6kA"]
["FI/LS-Schalter"]
["FI/LS-Schalter","FI/LS IDPN VIGI 1P+N 10A C 30MA A 110VAC","A9D01610",null,"Schneider",10,1.8,null,null,{"$f":"G539+I539","v":1.8},"FI/LS IDPN VIGI 1P+N 10A C 30MA A 110VAC"]
["FI/LS-Schalter","FI/LS IDPN VIGI 1P+N 16A C 30MA A 110VAC","A9D01616",null,"Schneider",16,3.2,null,null,3.2,"FI/LS IDPN VIGI 1P+N 16A C 30MA A 110VAC"]
["FI/LS-Schalter","FI/LS IDPN VIGI 1P+N 20A C 30MA A 110VAC","A9D01620",null,"Schneider",20,3.9,null,null,3.9,"FI/LS IDPN VIGI 1P+N 20A C 30MA A 110VAC"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 10A, 10mA Typ A","A9D02610",null,"Schneider",10,1.8,null,null,1.8,"FI/LS-Schalter iDPN N Vigi, 1p+N, 10A, 10mA Typ A"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 16A, 10mA Typ A","A9D02616",null,"Schneider",16,3.2,null,null,3.2,"FI/LS-Schalter iDPN N Vigi, 1p+N, 16A, 10mA Typ A"]
["FI/LS-Schalter","FI/LS IDPN VIGI 1P+N 10A B 30MA A 110VAC","A9D06610",null,"Schneider",10,1.8,null,null,1.8,"FI/LS IDPN VIGI 1P+N 10A B 30MA A 110VAC"]
["FI/LS-Schalter","FI/LS IDPN VIGI 1P+N 16A B 30MA A 110VAC","A9D06616",null,"Schneider",16,3.2,null,null,3.2,"FI/LS IDPN VIGI 1P+N 16A B 30MA A 110VAC"]
["FI/LS-Schalter","FI/LS IDPN VIGI 1P+N 20A B 30MA A 110VAC","A9D06620",null,"Schneider",20,3.9,null,null,3.9,"FI/LS IDPN VIGI 1P+N 20A B 30MA A 110VAC"]
["FI/LS-Schalter","FI/LS-Schalter iC60H 2P, 10A, C-Char., 30mA, Typ A, 10kA","A9D17210","10kA","Schneider",10,3.2,null,null,3.2,"FI/LS-Schalter iC60H 2P, 10A, C-Char., 30mA, Typ A, 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60H 2P, 13A, C-Char., 30mA, Typ A, 10kA","A9D17213","10kA","Schneider",13,4,null,null,4,"FI/LS-Schalter iC60H 2P, 13A, C-Char., 30mA, Typ A, 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60H 2P, 20A, C-Char., 30mA, Typ A, 10kA","A9D17220","10kA","Schneider",20,6.6,null,null,6.6,"FI/LS-Schalter iC60H 2P, 20A, C-Char., 30mA, Typ A, 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60H 2P, 25A, C-Char., 30mA, Typ A, 10kA","A9D17225","10kA","Schneider",25,7.6,null,null,7.6,"FI/LS-Schalter iC60H 2P, 25A, C-Char., 30mA, Typ A, 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60H 2P, 32A, C-Char., 30mA, Typ A, 10kA","A9D17232","10kA","Schneider",32,9.3000000000000007,null,null,9.3000000000000007,"FI/LS-Schalter iC60H 2P, 32A, C-Char., 30mA, Typ A, 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60H 3P, 13A, C-Char., 30mA, Typ A, 10kA, 230V AC","A9D17313","10kA","Schneider",13,4,null,null,4,"FI/LS-Schalter iC60H 3P, 13A, C-Char., 30mA, Typ A, 10kA, 230V AC"]
["FI/LS-Schalter","FI/LS-Schalter iC60H 2P, 10A, C-Char., 30mA, Typ A SI, 10kA","A9D27210","10kA","Schneider",10,3.2,null,null,3.2,"FI/LS-Schalter iC60H 2P, 10A, C-Char., 30mA, Typ A SI, 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60H 2P, 13A, C-Char., 30mA, Typ A SI, 10kA","A9D27213","10kA","Schneider",13,4,null,null,4,"FI/LS-Schalter iC60H 2P, 13A, C-Char., 30mA, Typ A SI, 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60H 2P, 16A, C-Char., 30mA, Typ A SI, 10kA","A9D27216","10kA","Schneider",16,4.9000000000000004,null,null,4.9000000000000004,"FI/LS-Schalter iC60H 2P, 16A, C-Char., 30mA, Typ A SI, 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60H 2P, 20A, C-Char., 30mA, Typ A SI, 10kA","A9D27220","10kA","Schneider",20,6.6,null,null,6.6,"FI/LS-Schalter iC60H 2P, 20A, C-Char., 30mA, Typ A SI, 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60H 2P, 25A, C-Char., 30mA, Typ A SI, 10kA","A9D27225","10kA","Schneider",25,7.6,null,null,7.6,"FI/LS-Schalter iC60H 2P, 25A, C-Char., 30mA, Typ A SI, 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60H 2P, 32A, C-Char., 30mA, Typ A SI, 10kA","A9D27232","10kA","Schneider",32,9.3000000000000007,null,null,9.3000000000000007,"FI/LS-Schalter iC60H 2P, 32A, C-Char., 30mA, Typ A SI, 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 6A, 30mA Typ SI C-Char., 6kA","A9D33606","6kA","Schneider",6,1.5,null,null,1.5,"FI/LS-Schalter iDPN N Vigi, 1p+N, 6A, 30mA Typ SI C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 10A, 30mA Typ SI C-Char., 6kA","A9D33610","6kA","Schneider",10,1.8,null,null,1.8,"FI/LS-Schalter iDPN N Vigi, 1p+N, 10A, 30mA Typ SI C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 13A, 30mA Typ SI C-Char., 6kA","A9D33613","6kA","Schneider",13,2.5,null,null,2.5,"FI/LS-Schalter iDPN N Vigi, 1p+N, 13A, 30mA Typ SI C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 16A, 30mA Typ SI C-Char., 6kA","A9D33616","6kA","Schneider",16,3.2,null,null,3.2,"FI/LS-Schalter iDPN N Vigi, 1p+N, 16A, 30mA Typ SI C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 20A, 30mA Typ SI C-Char., 6kA","A9D33620","6kA","Schneider",20,3.9,null,null,3.9,"FI/LS-Schalter iDPN N Vigi, 1p+N, 20A, 30mA Typ SI C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 25A, 30mA Typ SI C-Char., 6kA","A9D33625","6kA","Schneider",25,4.0999999999999996,null,null,4.0999999999999996,"FI/LS-Schalter iDPN N Vigi, 1p+N, 25A, 30mA Typ SI C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 32A, 30mA Typ SI C-Char., 6kA","A9D33632","6kA","Schneider",32,5.6,null,null,5.6,"FI/LS-Schalter iDPN N Vigi, 1p+N, 32A, 30mA Typ SI C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 40A, 30mA Typ SI C-Char., 6kA","A9D33640","6kA","Schneider",40,7,null,null,7,"FI/LS-Schalter iDPN N Vigi, 1p+N, 40A, 30mA Typ SI C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60H 2P, 13A, B-Char., 30mA, Typ A, 10kA","A9D37213","10kA","Schneider",13,2.5,null,null,2.5,"FI/LS-Schalter iC60H 2P, 13A, B-Char., 30mA, Typ A, 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN H Vigi, 1p+N, 6A, 30mA Typ A C-Char., 10kA","A9D37606","10kA","Schneider",6,1.5,null,null,1.5,"FI/LS-Schalter iDPN H Vigi, 1p+N, 6A, 30mA Typ A C-Char., 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN H Vigi, 1p+N, 10A, 30mA Typ A C-Char., 10kA","A9D37610","10kA","Schneider",10,1.8,null,null,1.8,"FI/LS-Schalter iDPN H Vigi, 1p+N, 10A, 30mA Typ A C-Char., 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN H Vigi, 1p+N, 20A, 30mA Typ A C-Char., 10kA","A9D37620","10kA","Schneider",20,3.9,null,null,3.9,"FI/LS-Schalter iDPN H Vigi, 1p+N, 20A, 30mA Typ A C-Char., 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN H Vigi, 1p+N, 32A, 30mA Typ A C-Char., 10kA","A9D37632","10kA","Schneider",32,5.6,null,null,5.6,"FI/LS-Schalter iDPN H Vigi, 1p+N, 32A, 30mA Typ A C-Char., 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN H Vigi, 1p+N, 6A, 30mA Typ SI C-Char., 10kA","A9D38606","10kA","Schneider",6,1.5,null,null,1.5,"FI/LS-Schalter iDPN H Vigi, 1p+N, 6A, 30mA Typ SI C-Char., 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN H Vigi, 1p+N, 10A, 30mA Typ SI C-Char., 10kA","A9D38610","10kA","Schneider",10,1.8,null,null,1.8,"FI/LS-Schalter iDPN H Vigi, 1p+N, 10A, 30mA Typ SI C-Char., 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN H Vigi, 1p+N, 16A, 30mA Typ SI C-Char., 10kA","A9D38616","10kA","Schneider",16,3.2,null,null,3.2,"FI/LS-Schalter iDPN H Vigi, 1p+N, 16A, 30mA Typ SI C-Char., 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN H Vigi, 1p+N, 20A, 30mA Typ SI C-Char., 10kA","A9D38620","10kA","Schneider",20,3.9,null,null,3.9,"FI/LS-Schalter iDPN H Vigi, 1p+N, 20A, 30mA Typ SI C-Char., 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN H Vigi, 1p+N, 25A, 30mA Typ SI C-Char., 10kA","A9D38625","10kA","Schneider",25,4.0999999999999996,null,null,4.0999999999999996,"FI/LS-Schalter iDPN H Vigi, 1p+N, 25A, 30mA Typ SI C-Char., 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN H Vigi, 1p+N, 32A, 30mA Typ SI C-Char., 10kA","A9D38632","10kA","Schneider",32,5.6,null,null,5.6,"FI/LS-Schalter iDPN H Vigi, 1p+N, 32A, 30mA Typ SI C-Char., 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 6A, 300mA Typ A C-Char., 6kA","A9D42606","6kA","Schneider",6,1.5,null,null,1.5,"FI/LS-Schalter iDPN N Vigi, 1p+N, 6A, 300mA Typ A C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 10A, 300mA Typ A C-Char., 6kA","A9D42610","6kA","Schneider",10,1.8,null,null,1.8,"FI/LS-Schalter iDPN N Vigi, 1p+N, 10A, 300mA Typ A C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 13A, 300mA Typ A C-Char., 6kA","A9D42613","6kA","Schneider",13,2.5,null,null,2.5,"FI/LS-Schalter iDPN N Vigi, 1p+N, 13A, 300mA Typ A C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 16A, 300mA Typ A C-Char., 6kA","A9D42616","6kA","Schneider",16,3.2,null,null,3.2,"FI/LS-Schalter iDPN N Vigi, 1p+N, 16A, 300mA Typ A C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 20A, 300mA Typ A C-Char., 6kA","A9D42620","6kA","Schneider",20,3.9,null,null,3.9,"FI/LS-Schalter iDPN N Vigi, 1p+N, 20A, 300mA Typ A C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 25A, 300mA Typ A C-Char., 6kA","A9D42625","6kA","Schneider",25,4.0999999999999996,null,null,4.0999999999999996,"FI/LS-Schalter iDPN N Vigi, 1p+N, 25A, 300mA Typ A C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 32A, 300mA Typ A C-Char., 6kA","A9D42632","6kA","Schneider",32,5.6,null,null,5.6,"FI/LS-Schalter iDPN N Vigi, 1p+N, 32A, 300mA Typ A C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 40A, 300mA Typ A C-Char., 6kA","A9D42640","6kA","Schneider",40,7,null,null,7,"FI/LS-Schalter iDPN N Vigi, 1p+N, 40A, 300mA Typ A C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 6A, 300mA Typ SI C-Char., 6kA","A9D43606","6kA","Schneider",6,1.5,null,null,1.5,"FI/LS-Schalter iDPN N Vigi, 1p+N, 6A, 300mA Typ SI C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 10A, 300mA Typ S IC-Char., 6kA","A9D43610","6kA","Schneider",10,1.8,null,null,1.8,"FI/LS-Schalter iDPN N Vigi, 1p+N, 10A, 300mA Typ S IC-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 13A, 300mA Typ S IC-Char., 6kA","A9D43613","6kA","Schneider",13,2.5,null,null,2.5,"FI/LS-Schalter iDPN N Vigi, 1p+N, 13A, 300mA Typ S IC-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 16A, 300mA Typ S C-Char., 6kA","A9D43616","6kA","Schneider",16,3.2,null,null,3.2,"FI/LS-Schalter iDPN N Vigi, 1p+N, 16A, 300mA Typ S C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 20A, 300mA Typ S C-Char., 6kA","A9D43620","6kA","Schneider",20,3.9,null,null,3.9,"FI/LS-Schalter iDPN N Vigi, 1p+N, 20A, 300mA Typ S C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 25A, 300mA Typ S C-Char., 6kA","A9D43625","6kA","Schneider",25,4.0999999999999996,null,null,4.0999999999999996,"FI/LS-Schalter iDPN N Vigi, 1p+N, 25A, 300mA Typ S C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 32A, 300mA Typ S C-Char., 6kA","A9D43632","6kA","Schneider",32,5.6,null,null,5.6,"FI/LS-Schalter iDPN N Vigi, 1p+N, 32A, 300mA Typ S C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 40A, 300mA Typ S C-Char., 6kA","A9D43640","6kA","Schneider",40,7,null,null,7,"FI/LS-Schalter iDPN N Vigi, 1p+N, 40A, 300mA Typ S C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60H 2P, 13A, B-Char., 30mA, Typ A SI, 10kA","A9D47213","10kA","Schneider",13,4.9000000000000004,null,null,4.9000000000000004,"FI/LS-Schalter iC60H 2P, 13A, B-Char., 30mA, Typ A SI, 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN H Vigi, 1p+N, 6A, 300mA Typ A C-Char., 10kA","A9D47606","10kA","Schneider",6,1.5,null,null,1.5,"FI/LS-Schalter iDPN H Vigi, 1p+N, 6A, 300mA Typ A C-Char., 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN H Vigi, 1p+N, 10A, 300mA Typ A C-Char., 10kA","A9D47610","10kA","Schneider",10,1.8,null,null,1.8,"FI/LS-Schalter iDPN H Vigi, 1p+N, 10A, 300mA Typ A C-Char., 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN H Vigi, 1p+N, 16A, 300mA Typ A C-Char., 10kA","A9D47616","10kA","Schneider",16,3.2,null,null,3.2,"FI/LS-Schalter iDPN H Vigi, 1p+N, 16A, 300mA Typ A C-Char., 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN H Vigi, 1p+N, 20A, 300mA Typ A C-Char., 10kA","A9D47620","10kA","Schneider",20,3.9,null,null,3.9,"FI/LS-Schalter iDPN H Vigi, 1p+N, 20A, 300mA Typ A C-Char., 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN H Vigi, 1p+N, 25A, 300mA Typ A C-Char., 10kA","A9D47625","10kA","Schneider",25,4.0999999999999996,null,null,4.0999999999999996,"FI/LS-Schalter iDPN H Vigi, 1p+N, 25A, 300mA Typ A C-Char., 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN H Vigi, 1p+N, 32A, 300mA Typ A C-Char., 10kA","A9D47632","10kA","Schneider",32,5.6,null,null,5.6,"FI/LS-Schalter iDPN H Vigi, 1p+N, 32A, 300mA Typ A C-Char., 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN H Vigi, 1p+N, 6A, 300mA Typ SI C-Char., 10kA","A9D48606","10kA","Schneider",6,1.5,null,null,1.5,"FI/LS-Schalter iDPN H Vigi, 1p+N, 6A, 300mA Typ SI C-Char., 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN H Vigi, 1p+N, 10A, 300mA Typ S C-Char., 10kA","A9D48610","10kA","Schneider",10,1.8,null,null,1.8,"FI/LS-Schalter iDPN H Vigi, 1p+N, 10A, 300mA Typ S C-Char., 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN H Vigi, 1p+N, 16A, 300mA Typ S C-Char., 10kA","A9D48616","10kA","Schneider",16,3.2,null,null,{"$f":"G603+I603","v":3.2},"FI/LS-Schalter iDPN H Vigi, 1p+N, 16A, 300mA Typ S C-Char., 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN H Vigi, 1p+N, 20A, 300mA Typ S C-Char., 10kA","A9D48620","10kA","Schneider",20,3.9,null,null,3.9,"FI/LS-Schalter iDPN H Vigi, 1p+N, 20A, 300mA Typ S C-Char., 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN H Vigi, 1p+N, 25A, 300mA Typ S IC-Char., 10kA","A9D48625","10kA","Schneider",25,4.0999999999999996,null,null,4.0999999999999996,"FI/LS-Schalter iDPN H Vigi, 1p+N, 25A, 300mA Typ S IC-Char., 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN H Vigi, 1p+N, 32A, 300mA Typ S IC-Char., 10kA","A9D48632","10kA","Schneider",32,5.6,null,null,5.6,"FI/LS-Schalter iDPN H Vigi, 1p+N, 32A, 300mA Typ S IC-Char., 10kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60N 4P, 10A, C-Char., 300mA, Typ A, 6kA","A9D52410","6kA","Schneider",10,3.2,null,null,3.2,"FI/LS-Schalter iC60N 4P, 10A, C-Char., 300mA, Typ A, 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60N 4P, 16A, C-Char., 300mA, Typ A, 6kA","A9D52416","6kA","Schneider",16,4.9000000000000004,null,null,4.9000000000000004,"FI/LS-Schalter iC60N 4P, 16A, C-Char., 300mA, Typ A, 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60N 4P, 20A, C-Char., 300mA, Typ A, 6kA","A9D52420","6kA","Schneider",20,6.8,null,null,6.8,"FI/LS-Schalter iC60N 4P, 20A, C-Char., 300mA, Typ A, 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60N 4P, 25A, C-Char., 300mA, Typ A, 6kA","A9D52425","6kA","Schneider",25,7.6,null,null,7.6,"FI/LS-Schalter iC60N 4P, 25A, C-Char., 300mA, Typ A, 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60N 4P, 32A, C-Char., 300mA, Typ A, 6kA","A9D52432","6kA","Schneider",32,9.3000000000000007,null,null,9.3000000000000007,"FI/LS-Schalter iC60N 4P, 32A, C-Char., 300mA, Typ A, 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 6A, 100mA Typ A C-Char., 6kA","A9D52606","6kA","Schneider",6,1.5,null,null,1.5,"FI/LS-Schalter iDPN N Vigi, 1p+N, 6A, 100mA Typ A C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 10A, 100mA Typ A C-Char., 6kA","A9D52610","6kA","Schneider",10,1.8,null,null,1.8,"FI/LS-Schalter iDPN N Vigi, 1p+N, 10A, 100mA Typ A C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 13A, 100mA Typ A C-Char., 6kA","A9D52613","6kA","Schneider",13,2.5,null,null,2.5,"FI/LS-Schalter iDPN N Vigi, 1p+N, 13A, 100mA Typ A C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 16A, 100mA Typ A C-Char., 6kA","A9D52616","6kA","Schneider",16,3.2,null,null,3.2,"FI/LS-Schalter iDPN N Vigi, 1p+N, 16A, 100mA Typ A C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 20A, 100mA Typ A C-Char., 6kA","A9D52620","6kA","Schneider",20,3.9,null,null,3.9,"FI/LS-Schalter iDPN N Vigi, 1p+N, 20A, 100mA Typ A C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 25A, 100mA Typ A C-Char., 6kA","A9D52625","6kA","Schneider",25,4.0999999999999996,null,null,4.0999999999999996,"FI/LS-Schalter iDPN N Vigi, 1p+N, 25A, 100mA Typ A C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 32A, 100mA Typ A C-Char., 6kA","A9D52632","6kA","Schneider",32,5.6,null,null,5.6,"FI/LS-Schalter iDPN N Vigi, 1p+N, 32A, 100mA Typ A C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 40A, 100mA Typ A C-Char., 6kA","A9D52640","6kA","Schneider",40,7,null,null,7,"FI/LS-Schalter iDPN N Vigi, 1p+N, 40A, 100mA Typ A C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 6A, 100mA Typ A C-Char., 6kA","A9D53606","6kA","Schneider",6,1.5,null,null,1.5,"FI/LS-Schalter iDPN N Vigi, 1p+N, 6A, 100mA Typ A C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 10A, 100mA Typ A C-Char., 6kA","A9D53610","6kA","Schneider",10,1.8,null,null,1.8,"FI/LS-Schalter iDPN N Vigi, 1p+N, 10A, 100mA Typ A C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 13A, 100mA Typ A C-Char., 6kA","A9D53613","6kA","Schneider",13,2.5,null,null,2.5,"FI/LS-Schalter iDPN N Vigi, 1p+N, 13A, 100mA Typ A C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 16A, 100mA Typ A C-Char., 6kA","A9D53616","6kA","Schneider",16,3.2,null,null,3.2,"FI/LS-Schalter iDPN N Vigi, 1p+N, 16A, 100mA Typ A C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 20A, 100mA Typ A C-Char., 6kA","A9D53620","6kA","Schneider",20,3.9,null,null,3.9,"FI/LS-Schalter iDPN N Vigi, 1p+N, 20A, 100mA Typ A C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 25A, 100mA Typ A C-Char., 6kA","A9D53625","6kA","Schneider",25,4.0999999999999996,null,null,4.0999999999999996,"FI/LS-Schalter iDPN N Vigi, 1p+N, 25A, 100mA Typ A C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 32A, 100mA Typ A C-Char., 6kA","A9D53632","6kA","Schneider",32,5.6,null,null,5.6,"FI/LS-Schalter iDPN N Vigi, 1p+N, 32A, 100mA Typ A C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iDPN N Vigi, 1p+N, 40A, 100mA Typ A C-Char., 6kA","A9D53640","6kA","Schneider",40,7,null,null,7,"FI/LS-Schalter iDPN N Vigi, 1p+N, 40A, 100mA Typ A C-Char., 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60N 3P, 13A, C-Char., 30mA, Typ A, 6kA","A9D67313","6kA","Schneider",13,4.9000000000000004,null,null,4.9000000000000004,"FI/LS-Schalter iC60N 3P, 13A, C-Char., 30mA, Typ A, 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60N 4P, 13A, C-Char., 30mA, Typ A, 6kA","A9D67413","6kA","Schneider",13,4.9000000000000004,null,null,4.9000000000000004,"FI/LS-Schalter iC60N 4P, 13A, C-Char., 30mA, Typ A, 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60N 4P, 10A, C-Char., 30mA, Typ A SI, 6kA","A9D77410","6kA","Schneider",10,3.2,null,null,3.2,"FI/LS-Schalter iC60N 4P, 10A, C-Char., 30mA, Typ A SI, 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60N 4P, 13A, C-Char., 30mA, Typ A SI, 6kA","A9D77413","6kA","Schneider",13,4.9000000000000004,null,null,4.9000000000000004,"FI/LS-Schalter iC60N 4P, 13A, C-Char., 30mA, Typ A SI, 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60N 4P, 20A, C-Char., 30mA, Typ A SI, 6kA","A9D77420","6kA","Schneider",20,6.8,null,null,6.8,"FI/LS-Schalter iC60N 4P, 20A, C-Char., 30mA, Typ A SI, 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60N 4P, 25A, C-Char., 30mA, Typ A SI, 6kA","A9D77425","6kA","Schneider",25,7.6,null,null,7.6,"FI/LS-Schalter iC60N 4P, 25A, C-Char., 30mA, Typ A SI, 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60N 4P, 13A, B-Char., 30mA, Typ A, 6kA","A9D87413","6kA","Schneider",13,4.9000000000000004,null,null,4.9000000000000004,"FI/LS-Schalter iC60N 4P, 13A, B-Char., 30mA, Typ A, 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60N 4P, 10A, B-Char., 30mA, Typ A SI, 6kA","A9D97410","6kA","Schneider",10,3.2,null,null,3.2,"FI/LS-Schalter iC60N 4P, 10A, B-Char., 30mA, Typ A SI, 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60N 4P, 13A, B-Char., 30mA, Typ A SI, 6kA","A9D97413","6kA","Schneider",13,4.9000000000000004,null,null,4.9000000000000004,"FI/LS-Schalter iC60N 4P, 13A, B-Char., 30mA, Typ A SI, 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60N 4P, 20A, B-Char., 30mA, Typ A SI, 6kA","A9D97420","6kA","Schneider",20,6.8,null,null,6.8,"FI/LS-Schalter iC60N 4P, 20A, B-Char., 30mA, Typ A SI, 6kA"]
["FI/LS-Schalter","FI/LS-Schalter iC60N 4P, 25A, B-Char., 30mA, Typ A SI, 6kA","A9D97425","6kA","Schneider",25,7.6,null,null,7.6,"FI/LS-Schalter iC60N 4P, 25A, B-Char., 30mA, Typ A SI, 6kA"]
[null,null,null,null,null,null,null,null,null,0]
["FI-Schalter","FI 2P ,  30mA","Acti9",null,"Schneider",null,null,null,null,0,"FI 2P ,  30mA"]
["FI-Schalter","FI-Schutzschalter iID, 2P, 25A , 30mA, Typ A","A9Z21225",null,"Schneider",25,3.2,{"$f":"G641*2","v":6.4},null,3.2,"FI-Schutzschalter iID, 2P, 25A , 30mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 2P, 40A , 30mA, Typ A","A9Z21240",null,"Schneider",40,3.8,{"$f":"G642*2","v":7.6},null,3.8,"FI-Schutzschalter iID, 2P, 40A , 30mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 2P, 63A , 30mA, Typ A","A9Z21263",null,"Schneider",63,3.5,7,null,3.5,"FI-Schutzschalter iID, 2P, 63A , 30mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 2P, 80A , 30mA, Typ A","A9Z21280",null,"Schneider",80,5.6,11.2,null,5.6,"FI-Schutzschalter iID, 2P, 80A , 30mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 2P, 100A , 30mA, Typ A","A9Z21291",null,"Schneider",100,7,14,null,7,"FI-Schutzschalter iID, 2P, 100A , 30mA, Typ A"]
["FI-Schalter",null,null,null,null,null,null,null,null,0,"Fehlerstrom-Schutzschalter Allstromsensitiv iID, 4P, 25A, Typ B-SI, 30mA"]
["FI-Schalter","Fehlerstrom-Schutzschalter Allstromsensitiv iID, 4P, 25A, Typ B-SI, 30mA","A9Z61425",null,"Schneider",25,3.2,{"$f":"G647*2","v":6.4},null,3.2,"Fehlerstrom-Schutzschalter (FI) Allstromsensitiv Acti9-iID, 4-polig, 40A, 30mA, Typ B-SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter (FI) Allstromsensitiv Acti9-iID, 4-polig, 40A, 30mA, Typ B-SI","A9Z61440",null,"Schneider",40,3.8,{"$f":"G648*2","v":7.6},null,3.8,"Fehlerstrom-Schutzschalter Allstromsensitiv iID, 4P, 63A, Typ B-SI, 30mA"]
["FI-Schalter","Fehlerstrom-Schutzschalter Allstromsensitiv iID, 4P, 63A, Typ B-SI, 30mA","A9Z61463",null,"Schneider",63,3.5,7,null,3.5,"Fehlerstrom-Schutzschalter Allstromsensitiv iID, 4P, 80A, Typ B-SI, 30mA"]
["FI-Schalter","Fehlerstrom-Schutzschalter Allstromsensitiv iID, 4P, 80A, Typ B-SI, 30mA","A9Z61480",null,"Schneider",80,5.6,11.2,null,5.6,"allstromsensitiv"]
["FI-Schalter",null,null,null,null,null,null,null,null,0]
["FI-Schalter","FI 2P ,  100mA","Acti9",null,"Schneider",null,null,null,null,0,"FI 2P ,  100mA"]
["FI-Schalter","FI-Schutzschalter iID, 2P, 40A , 100mA, Typ A","A9Z22240",null,"Schneider",40,3.8,{"$f":"G653*2","v":7.6},null,{"$f":"G653+I653","v":3.8},"FI-Schutzschalter iID, 2P, 40A , 100mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 2P, 63A , 100mA, Typ A","A9Z22263",null,"Schneider",63,3.5,7,null,3.5,"FI-Schutzschalter iID, 2P, 63A , 100mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 2P, 80A , 100mA, Typ A","A9Z22280",null,"Schneider",80,5.6,11.2,null,5.6,"FI-Schutzschalter iID, 2P, 80A , 100mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 2P, 100A , 100mA, Typ A","A9Z22291",null,"Schneider",100,7,14,null,7,"FI-Schutzschalter iID, 2P, 100A , 100mA, Typ A"]
["FI-Schalter",null,null,null,null,null,null,null,null,0]
["FI-Schalter","FI 2P ,  300mA","Acti9",null,"Schneider",null,null,null,null,0,"FI 2P ,  300mA"]
["FI-Schalter","FI-Schutzschalter iID, 2P, 25A , 300mA, Typ A","A9Z24225",null,"Schneider",25,3.2,{"$f":"G659*2","v":6.4},null,3.2,"FI-Schutzschalter iID, 2P, 25A , 300mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 2P, 40A , 300mA, Typ A","A9Z24240",null,"Schneider",40,3.8,{"$f":"G660*2","v":7.6},null,3.8,"FI-Schutzschalter iID, 2P, 40A , 300mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 2P, 63A , 300mA, Typ A","A9Z24263",null,"Schneider",63,3.5,7,null,3.5,"FI-Schutzschalter iID, 2P, 63A , 300mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 2P, 80A , 300mA, Typ A","A9Z24280",null,"Schneider",80,5.6,11.2,null,5.6,"FI-Schutzschalter iID, 2P, 80A , 300mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 2P, 100A , 300mA, Typ A","A9Z24291",null,"Schneider",100,7,14,null,7,"FI-Schutzschalter iID, 2P, 100A , 300mA, Typ A"]
["FI-Schalter","FI Allstromsensitiv iID,300mA",null,null,null,null,null,null,null,0,"allstromsensitiv"]
["FI-Schalter","Fehlerstrom-Schutzschalter Allstromsensitiv iID, 4P, 25A, Typ B-SI, 300mA","A9Z64425",null,"Schneider",25,3.2,null,null,3.2,"allstromsensitiv"]
["FI-Schalter","Fehlerstrom-Schutzschalter Allstromsensitiv iID, 4P, 40A, Typ B-SI, 300mA","A9Z64440",null,"Schneider",40,3.8,null,null,3.8,"allstromsensitiv"]
["FI-Schalter","Fehlerstrom-Schutzschalter Allstromsensitiv iID, 4P, 63A, Typ B-SI, 300mA","A9Z64463",null,"Schneider",63,3.5,null,null,3.5,"allstromsensitiv"]
["FI-Schalter","Fehlerstrom-Schutzschalter Allstromsensitiv iID, 4P, 80A, Typ B-SI, 300mA","A9Z64480",null,"Schneider",80,5.6,null,null,5.6,"allstromsensitiv"]
["FI-Schalter",null,null,null,null,null,null,null,null,0]
["FI-Schalter","FI 4P ,  30mA","Acti9",null,"Schneider",null,null,null,null,0,"FI 4P ,  30mA"]
["FI-Schalter","FI-Schutzschalter iID, 4P, 25A , 30mA, Typ A","A9Z21425",null,"Schneider",25,3.2,{"$f":"G671*3","v":9.6000000000000014},null,3.2,"FI-Schutzschalter iID, 4P, 25A , 30mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 4P, 40A , 30mA, Typ A","A9Z21440",null,"Schneider",40,3.8,{"$f":"G672*3","v":11.399999999999999},null,3.8,"FI-Schutzschalter iID, 4P, 40A , 30mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 4P, 63A , 30mA, Typ A","A9Z21463",null,"Schneider",63,3.5,10.5,null,3.5,"FI-Schutzschalter iID, 4P, 63A , 30mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 4P, 80A , 30mA, Typ A","A9Z21480",null,"Schneider",80,5.6,16.799999999999997,null,5.6,"FI-Schutzschalter iID, 4P, 80A , 30mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 4P, 100A , 30mA, Typ A","A9Z21491",null,"Schneider",100,7,21,null,7,"FI-Schutzschalter iID, 4P, 100A , 30mA, Typ A"]
["FI-Schalter",null,null,null,null,null,null,null,null,0]
["FI-Schalter","FI 4P ,  100mA","Acti9",null,"Schneider",null,null,null,null,0,"FI 4P ,  100mA"]
["FI-Schalter","FI-Schutzschalter iID, 4P, 40A , 100mA, Typ A","A9Z22440",null,"Schneider",40,3.8,{"$f":"G678*3","v":11.399999999999999},null,3.8,"FI-Schutzschalter iID, 4P, 40A , 100mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 4P, 63A , 100mA, Typ A","A9Z22463",null,"Schneider",63,3.5,10.5,null,3.5,"FI-Schutzschalter iID, 4P, 63A , 100mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 4P, 80A , 100mA, Typ A","A9Z22480",null,"Schneider",80,5.6,16.799999999999997,null,5.6,"FI-Schutzschalter iID, 4P, 80A , 100mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 4P, 100A , 100mA, Typ A","A9Z22491",null,"Schneider",100,7,21,null,7,"FI-Schutzschalter iID, 4P, 100A , 100mA, Typ A"]
["FI-Schalter",null,null,null,null,null,null,null,null,0]
["FI-Schalter","FI 4P ,  300mA","Acti9",null,"Schneider",null,null,null,null,0,"FI 4P ,  300mA"]
["FI-Schalter","FI-Schutzschalter iID, 4P, 25A , 300mA, Typ A","A9Z24425",null,"Schneider",25,3.2,{"$f":"G684*3","v":9.6000000000000014},null,3.2,"FI-Schutzschalter iID, 4P, 25A , 300mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 4P, 40A , 300mA, Typ A","A9Z24440",null,"Schneider",40,3.8,{"$f":"G685*3","v":11.399999999999999},null,3.8,"FI-Schutzschalter iID, 4P, 40A , 300mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 4P, 63A , 300mA, Typ A","A9Z24463",null,"Schneider",63,3.5,10.5,null,3.5,"FI-Schutzschalter iID, 4P, 63A , 300mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 4P, 80A , 300mA, Typ A","A9Z24480",null,"Schneider",80,5.6,16.799999999999997,null,5.6,"FI-Schutzschalter iID, 4P, 80A , 300mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 4P, 100A , 300mA, Typ A","A9Z24491",null,"Schneider",100,7,21,null,7,"FI-Schutzschalter iID, 4P, 100A , 300mA, Typ A"]
["FI-Schalter",null,null,null,null,null,null,null,null,0]
["FI-Schalter","FI 4P ,  500mA","Acti9",null,"Schneider",null,null,null,null,0,"FI 4P ,  500mA"]
["FI-Schalter","FI-Schutzschalter iID, 4P, 25A , 500mA, Typ A","A9Z26425",null,"Schneider",25,3.2,{"$f":"G691*3","v":9.6000000000000014},null,3.2,"FI-Schutzschalter iID, 4P, 25A , 500mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 4P, 40A , 500mA, Typ A","A9Z26440",null,"Schneider",40,3.8,{"$f":"G692*3","v":11.399999999999999},null,3.8,"FI-Schutzschalter iID, 4P, 40A , 500mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 4P, 63A , 500mA, Typ A","A9Z26463",null,"Schneider",63,3.5,10.5,null,3.5,"FI-Schutzschalter iID, 4P, 63A , 500mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 4P, 80A , 500mA, Typ A","A9Z26480",null,"Schneider",80,5.6,16.799999999999997,null,5.6,"FI-Schutzschalter iID, 4P, 80A , 500mA, Typ A"]
["FI-Schalter","FI-Schutzschalter iID, 4P, 100A , 500mA, Typ A","A9Z26491",null,"Schneider",100,7,21,null,7,"FI-Schutzschalter iID, 4P, 100A , 500mA, Typ A"]
["FI-Schalter"]
["FI-Schalter","Fehlerstrom-Schutzschalter ID, 4P, 125A, Typ B, 300mA",16764,null,"Schneider",125,7,null,null,{"$f":"G697+I697","v":7},"Fehlerstrom-Schutzschalter ID, 4P, 125A, Typ B, 300mA"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 4p, 63A , 300mA, T yp A selektiv","A9Z25463",null,"Schneider",63,3.5,null,null,3.5,"Fehlerstrom-Schutzschalter iID, 4p, 63A , 300mA, T yp A selektiv"]
["FI-Schalter","Fehlerstrom-Schutzschalter 2P, 40A, Typ B-EV, 30mA Elektroladestation iID","A9Z51240",null,"Schneider",40,1.8,null,null,1.8,"Fehlerstrom-Schutzschalter 2P, 40A, Typ B-EV, 30mA Elektroladestation iID"]
["FI-Schalter","FI-SCHALTER IID 4P 25A 30MA TYP B-EV","A9Z51425",null,"Schneider",40,0.7,null,null,0.7,"FI-SCHALTER IID 4P 25A 30MA TYP B-EV"]
["FI-Schalter","Fehlerstrom-Schutzschalter 4P, 40A, Typ B-EV, 30mA Elektroladestation iID","A9Z51440",null,"Schneider",40,0.7,null,null,0.7,"Fehlerstrom-Schutzschalter 4P, 40A, Typ B-EV, 30mA Elektroladestation iID"]
["FI-Schalter","FI-SCHALTER IID 4P 40A 300MA S TYP B-SI","A9Z65440",null,"Schneider",40,0.7,null,null,0.7,"FI-SCHALTER IID 4P 40A 300MA S TYP B-SI"]
["FI-Schalter","FI-SCHALTER IID 4P 80A 300MA S TYP B-SI","A9Z65480",null,"Schneider",80,7.3,null,null,7.3,"FI-SCHALTER IID 4P 80A 300MA S TYP B-SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter Resi9 1P+N, 25A, 30mA, Typ A","R9R22225",null,"Schneider",25,1.4,null,null,1.4,"Fehlerstrom-Schutzschalter Resi9 1P+N, 25A, 30mA, Typ A"]
["FI-Schalter","Fehlerstrom-Schutzschalter Resi9 1P+N, 40A, 30mA, Typ A","R9R22240",null,"Schneider",40,3.6,null,null,3.6,"Fehlerstrom-Schutzschalter Resi9 1P+N, 40A, 30mA, Typ A"]
["FI-Schalter","Fehlerstrom-Schutzschalter Resi9 3P+N, 40A, 30mA,  Typ A","R9R22440",null,"Schneider",40,3.6,null,null,3.6,"Fehlerstrom-Schutzschalter Resi9 3P+N, 40A, 30mA,  Typ A"]
["FI-Schalter","Fehlerstrom-Schutzschalter Resi9 3P+N, 63A, 30mA, Typ A","R9R22463",null,"Schneider",63,4.4000000000000004,null,null,4.4000000000000004,"Fehlerstrom-Schutzschalter Resi9 3P+N, 63A, 30mA, Typ A"]
["FI-Schalter","Fehlerstrom-Schutzschalter Resi9 3P+N, 40A, 30mA, Typ F","R9R42440",null,"Schneider",40,3.6,null,null,3.6,"Fehlerstrom-Schutzschalter Resi9 3P+N, 40A, 30mA, Typ F"]
["FI-Schalter","Fehlerstrom-Schutzschalter ID K, 2p, 25A, 30mA, Ty p A","A9Z01225",null,"Schneider",25,2.7,null,null,2.7,"Fehlerstrom-Schutzschalter ID K, 2p, 25A, 30mA, Ty p A"]
["FI-Schalter","Fehlerstrom-Schutzschalter ID K, 2p, 40A, 30mA, Ty p A","A9Z01240",null,"Schneider",40,3.6,null,null,3.6,"Fehlerstrom-Schutzschalter ID K, 2p, 40A, 30mA, Ty p A"]
["FI-Schalter","Fehlerstrom-Schutzschalter ID K, 4p, 40A, 30mA, Ty p A","A9Z01440",null,"Schneider",40,3.6,null,null,3.6,"Fehlerstrom-Schutzschalter ID K, 4p, 40A, 30mA, Ty p A"]
["FI-Schalter","Fehlerstrom-Schutzschalter ID K, 4p, 40A, 300mA, T yp A","A9Z04440",null,"Schneider",40,3.6,null,null,3.6,"Fehlerstrom-Schutzschalter ID K, 4p, 40A, 300mA, T yp A"]
["FI-Schalter","Fehlerstrom-Schutzschalter ID K, 4p, 63A, 300mA, T yp A","A9Z04463",null,"Schneider",63,5.6,null,null,5.6,"Fehlerstrom-Schutzschalter ID K, 4p, 63A, 300mA, T yp A"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 2p, 40A , 300mA, T yp A selektiv","A9Z25240",null,"Schneider",40,3.6,null,null,3.6,"Fehlerstrom-Schutzschalter iID, 2p, 40A , 300mA, T yp A selektiv"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 2p, 63A , 300mA, T yp A selektiv","A9Z25263",null,"Schneider",63,5.6,null,null,5.6,"Fehlerstrom-Schutzschalter iID, 2p, 63A , 300mA, T yp A selektiv"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 2p, 80A , 300mA, T yp A selektiv","A9Z25280",null,"Schneider",80,5.6,null,null,5.6,"Fehlerstrom-Schutzschalter iID, 2p, 80A , 300mA, T yp A selektiv"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 2p, 100A , 300mA,  Typ A selektiv","A9Z25291",null,"Schneider",100,7,null,null,7,"Fehlerstrom-Schutzschalter iID, 2p, 100A , 300mA,  Typ A selektiv"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 4p, 80A , 300mA, T yp A selektiv","A9Z25480",null,"Schneider",80,5.6,null,null,5.6,"Fehlerstrom-Schutzschalter iID, 4p, 80A , 300mA, T yp A selektiv"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 4p, 100A , 300mA,  Typ A selektiv","A9Z25491",null,"Schneider",100,7,null,null,7,"Fehlerstrom-Schutzschalter iID, 4p, 100A , 300mA,  Typ A selektiv"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 2p, 25A , 10mA, Ty p A, SI","A9Z30225",null,"Schneider",25,3.2,null,null,3.2,"Fehlerstrom-Schutzschalter iID, 2p, 25A , 10mA, Ty p A, SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 2p, 40A , 30mA, Ty p A, SI","A9Z31240",null,"Schneider",40,3.8,null,null,3.8,"Fehlerstrom-Schutzschalter iID, 2p, 40A , 30mA, Ty p A, SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 2p, 63A , 30mA, Ty p A, SI","A9Z31263",null,"Schneider",63,3.5,null,null,3.5,"Fehlerstrom-Schutzschalter iID, 2p, 63A , 30mA, Ty p A, SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 2p, 80A , 30mA, Ty p A, SI","A9Z31280",null,"Schneider",80,5.6,null,null,5.6,"Fehlerstrom-Schutzschalter iID, 2p, 80A , 30mA, Ty p A, SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 2p, 100A , 30mA, T yp A, SI","A9Z31291",null,"Schneider",100,7,null,null,7,"Fehlerstrom-Schutzschalter iID, 2p, 100A , 30mA, T yp A, SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 4p, 25A , 30mA, Ty p A, SI","A9Z31425",null,"Schneider",25,3.2,null,null,3.2,"Fehlerstrom-Schutzschalter iID, 4p, 25A , 30mA, Ty p A, SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 4p, 40A , 30mA, Ty p A, SI","A9Z31440",null,"Schneider",40,3.8,null,null,3.8,"Fehlerstrom-Schutzschalter iID, 4p, 40A , 30mA, Ty p A, SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 4p, 63A , 30mA, Ty p A, SI","A9Z31463",null,"Schneider",63,3.5,null,null,3.5,"Fehlerstrom-Schutzschalter iID, 4p, 63A , 30mA, Ty p A, SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 4p, 80A , 30mA, Ty p A, SI","A9Z31480",null,"Schneider",80,5.6,null,null,5.6,"Fehlerstrom-Schutzschalter iID, 4p, 80A , 30mA, Ty p A, SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 4p, 100A , 30mA, T yp A, SI","A9Z31491",null,"Schneider",100,7,null,null,{"$f":"G729+I729","v":7},"Fehlerstrom-Schutzschalter iID, 4p, 100A , 30mA, T yp A, SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 2p, 40A , 100mA, T yp A, SI","A9Z32240",null,"Schneider",40,3.8,null,null,3.8,"Fehlerstrom-Schutzschalter iID, 2p, 40A , 100mA, T yp A, SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 2p, 63A , 100mA, T yp A, SI","A9Z32263",null,"Schneider",63,3.5,null,null,3.5,"Fehlerstrom-Schutzschalter iID, 2p, 63A , 100mA, T yp A, SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 2p, 80A , 100mA, T yp A, SI","A9Z32280",null,"Schneider",80,5.6,null,null,5.6,"Fehlerstrom-Schutzschalter iID, 2p, 80A , 100mA, T yp A, SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 2p, 100A , 100mA,  Typ A, SI","A9Z32291",null,"Schneider",100,7,null,null,7,"Fehlerstrom-Schutzschalter iID, 2p, 100A , 100mA,  Typ A, SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 4p, 40A , 100mA, T yp A, SI","A9Z32440",null,"Schneider",40,3.8,null,null,3.8,"Fehlerstrom-Schutzschalter iID, 4p, 40A , 100mA, T yp A, SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 4p, 63A , 100mA, T yp A, SI","A9Z32463",null,"Schneider",63,3.5,null,null,3.5,"Fehlerstrom-Schutzschalter iID, 4p, 63A , 100mA, T yp A, SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 4p, 80A , 100mA, T yp A, SI","A9Z32480",null,"Schneider",80,5.6,null,null,5.6,"Fehlerstrom-Schutzschalter iID, 4p, 80A , 100mA, T yp A, SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 4p, 100A , 100mA,  Typ A, SI","A9Z32491",null,"Schneider",100,7,null,null,7,"Fehlerstrom-Schutzschalter iID, 4p, 100A , 100mA,  Typ A, SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 2p, 40A , 300mA, T yp A, SI","A9Z35240",null,"Schneider",40,3.8,null,null,3.8,"Fehlerstrom-Schutzschalter iID, 2p, 40A , 300mA, T yp A, SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 2p, 63A , 300mA, T yp A, SI","A9Z35263",null,"Schneider",63,3.5,null,null,3.5,"Fehlerstrom-Schutzschalter iID, 2p, 63A , 300mA, T yp A, SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 2p, 80A , 300mA, T yp A, SI","A9Z35280",null,"Schneider",80,5.6,null,null,5.6,"Fehlerstrom-Schutzschalter iID, 2p, 80A , 300mA, T yp A, SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 2p, 100A , 300mA,  Typ A, SI","A9Z35291",null,"Schneider",100,7,null,null,7,"Fehlerstrom-Schutzschalter iID, 2p, 100A , 300mA,  Typ A, SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 4p, 40A , 300mA, T yp A, SI","A9Z35440",null,"Schneider",40,3.8,null,null,3.8,"Fehlerstrom-Schutzschalter iID, 4p, 40A , 300mA, T yp A, SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 4p, 63A , 300mA, T yp A, SI","A9Z35463",null,"Schneider",63,3.5,null,null,3.5,"Fehlerstrom-Schutzschalter iID, 4p, 63A , 300mA, T yp A, SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 4p, 80A , 300mA, T yp A, SI","A9Z35480",null,"Schneider",80,5.6,null,null,5.6,"Fehlerstrom-Schutzschalter iID, 4p, 80A , 300mA, T yp A, SI"]
["FI-Schalter","Fehlerstrom-Schutzschalter iID, 4p, 100A , 300mA,  Typ A, SI","A9Z35491",null,"Schneider",100,7,null,null,7,"Fehlerstrom-Schutzschalter iID, 4p, 100A , 300mA,  Typ A, SI"]
["FI-Schalter","FI-SCHALTER IID 4P 63A 300MA S TYP B-SI","A9Z65463",null,"Schneider",63,3.5,null,null,3.5,"FI-SCHALTER IID 4P 63A 300MA S TYP B-SI"]
[null,null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  1P","Acti9","10kA","Schneider",null,null,null,null,0,"LS-Schalter  1P"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 6A, B Charakteristik","A9F06106","10kA","Schneider",6,1.3,1.3,null,1.3,"LS-Schalter iC60H, 1P, 6A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 10A, B Charakteristik","A9F06110","10kA","Schneider",10,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60H, 1P, 10A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 13A, B Charakteristik","A9F06113","10kA","Schneider",13,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60H, 1P, 13A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 16A, B Charakteristik","A9F06116","10kA","Schneider",16,2.4,2.4,null,2.4,"LS-Schalter iC60H, 1P, 16A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 20A, B Charakteristik","A9F06120","10kA","Schneider",20,2.4,2.4,null,2.4,"LS-Schalter iC60H, 1P, 20A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 25A, B Charakteristik","A9F06125","10kA","Schneider",25,3,3,null,3,"LS-Schalter iC60H, 1P, 25A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 32A, B Charakteristik","A9F06132","10kA","Schneider",32,2.8,2.8,null,2.8,"LS-Schalter iC60H, 1P, 32A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 40A, B Charakteristik","A9F06140","10kA","Schneider",40,3.6,3.6,null,3.6,"LS-Schalter iC60H, 1P, 40A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 50A, B Charakteristik","A9F06150","10kA","Schneider",50,4,4,null,4,"LS-Schalter iC60H, 1P, 50A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 63A, B Charakteristik","A9F06163","10kA","Schneider",63,5.6,5.6,null,5.6,"LS-Schalter iC60H, 1P, 63A, B Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  1P+N","Acti9","10kA","Schneider",null,null,null,null,0,"LS-Schalter  1P+N"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P+N, 6A, B Charakteristik","A9F06606","10kA","Schneider",6,1.3,1.3,null,1.3,"LS-Schalter iC60H, 1P+N, 6A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P+N, 10A, B Charakteristik","A9F06610","10kA","Schneider",10,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60H, 1P+N, 10A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P+N, 13A, B Charakteristik","A9F06613","10kA","Schneider",13,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60H, 1P+N, 13A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P+N, 16A, B Charakteristik","A9F06616","10kA","Schneider",16,2.4,2.4,null,2.4,"LS-Schalter iC60H, 1P+N, 16A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P+N, 20A, B Charakteristik","A9F06620","10kA","Schneider",20,2.4,2.4,null,2.4,"LS-Schalter iC60H, 1P+N, 20A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P+N, 25A, B Charakteristik","A9F06625","10kA","Schneider",25,3,3,null,3,"LS-Schalter iC60H, 1P+N, 25A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P+N, 32A, B Charakteristik","A9F06632","10kA","Schneider",32,2.8,2.8,null,2.8,"LS-Schalter iC60H, 1P+N, 32A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P+N, 40A, B Charakteristik","A9F06640","10kA","Schneider",40,3.6,3.6,null,{"$f":"G768+I768","v":3.6},"LS-Schalter iC60H, 1P+N, 40A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P+N, 50A, B Charakteristik","A9F06650","10kA","Schneider",50,4,4,null,4,"LS-Schalter iC60H, 1P+N, 50A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P+N, 63A, B Charakteristik","A9F06663","10kA","Schneider",63,5.6,5.6,null,5.6,"LS-Schalter iC60H, 1P+N, 63A, B Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  2P","Acti9","10kA","Schneider",null,null,null,null,0,"LS-Schalter  2P"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 6A, B Charakteristik","A9F06206","10kA","Schneider",6,1.3,{"$f":"2*G773","v":2.6},null,1.3,"LS-Schalter iC60H, 2P, 6A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 10A, B Charakteristik","A9F06210","10kA","Schneider",10,2.2999999999999998,{"$f":"2*G774","v":4.5999999999999996},null,2.2999999999999998,"LS-Schalter iC60H, 2P, 10A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 13A, B Charakteristik","A9F06213","10kA","Schneider",13,2.2999999999999998,4.5999999999999996,null,2.2999999999999998,"LS-Schalter iC60H, 2P, 13A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 16A, B Charakteristik","A9F06216","10kA","Schneider",16,2.4,4.8,null,2.4,"LS-Schalter iC60H, 2P, 16A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 20A, B Charakteristik","A9F06220","10kA","Schneider",20,2.4,4.8,null,2.4,"LS-Schalter iC60H, 2P, 20A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 25A, B Charakteristik","A9F06225","10kA","Schneider",25,3,6,null,3,"LS-Schalter iC60H, 2P, 25A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 32A, B Charakteristik","A9F06232","10kA","Schneider",32,2.8,5.6,null,2.8,"LS-Schalter iC60H, 2P, 32A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 40A, B Charakteristik","A9F06240","10kA","Schneider",40,3.6,7.2,null,3.6,"LS-Schalter iC60H, 2P, 40A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 50A, B Charakteristik","A9F06250","10kA","Schneider",50,4,8,null,4,"LS-Schalter iC60H, 2P, 50A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 63A, B Charakteristik","A9F06263","10kA","Schneider",63,5.6,11.2,null,5.6,"LS-Schalter iC60H, 2P, 63A, B Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  3P","Acti9","10kA","Schneider",null,null,null,null,0,"LS-Schalter  3P"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 6A, B Charakteristik","A9F06306","10kA","Schneider",6,1.3,{"$f":"G785*3","v":3.9000000000000004},null,1.3,"LS-Schalter iC60H, 3P, 6A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 10A, B Charakteristik","A9F06310","10kA","Schneider",10,2.2999999999999998,{"$f":"G786*3","v":6.8999999999999995},null,2.2999999999999998,"LS-Schalter iC60H, 3P, 10A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 13A, B Charakteristik","A9F06313","10kA","Schneider",13,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60H, 3P, 13A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 16A, B Charakteristik","A9F06316","10kA","Schneider",16,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60H, 3P, 16A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 20A, B Charakteristik","A9F06320","10kA","Schneider",20,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60H, 3P, 20A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 25A, B Charakteristik","A9F06325","10kA","Schneider",25,3,9,null,3,"LS-Schalter iC60H, 3P, 25A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 32A, B Charakteristik","A9F06332","10kA","Schneider",32,2.8,8.3999999999999986,null,2.8,"LS-Schalter iC60H, 3P, 32A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 40A, B Charakteristik","A9F06340","10kA","Schneider",40,3.6,10.8,null,3.6,"LS-Schalter iC60H, 3P, 40A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 50A, B Charakteristik","A9F06350","10kA","Schneider",50,4,12,null,4,"LS-Schalter iC60H, 3P, 50A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 63A, B Charakteristik","A9F06363","10kA","Schneider",63,5.6,16.799999999999997,null,5.6,"LS-Schalter iC60H, 3P, 63A, B Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  4P","Acti9","10kA","Schneider",null,null,null,null,0,"LS-Schalter  4P"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 6A, B Charakteristik","A9F06406","10kA","Schneider",6,1.3,{"$f":"G797*3","v":3.9000000000000004},null,1.3,"LS-Schalter iC60H, 4P, 6A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 10A, B Charakteristik","A9F06410","10kA","Schneider",10,2.2999999999999998,{"$f":"G798*3","v":6.8999999999999995},null,2.2999999999999998,"LS-Schalter iC60H, 4P, 10A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 13A, B Charakteristik","A9F06413","10kA","Schneider",13,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60H, 4P, 13A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 16A, B Charakteristik","A9F06416","10kA","Schneider",16,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60H, 4P, 16A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 20A, B Charakteristik","A9F06420","10kA","Schneider",20,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60H, 4P, 20A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 25A, B Charakteristik","A9F06425","10kA","Schneider",25,3,9,null,3,"LS-Schalter iC60H, 4P, 25A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 32A, B Charakteristik","A9F06432","10kA","Schneider",32,2.8,8.3999999999999986,null,2.8,"LS-Schalter iC60H, 4P, 32A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 40A, B Charakteristik","A9F06440","10kA","Schneider",40,3.6,10.8,null,3.6,"LS-Schalter iC60H, 4P, 40A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 50A, B Charakteristik","A9F06450","10kA","Schneider",50,4,12,null,4,"LS-Schalter iC60H, 4P, 50A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 63A, B Charakteristik","A9F06463","10kA","Schneider",63,5.6,16.799999999999997,null,5.6,"LS-Schalter iC60H, 4P, 63A, B Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  1P","Acti9","10kA","Schneider",null,null,null,null,0,"LS-Schalter  1P"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 1A, C Charakteristik","A9F07101","10kA","Schneider",1,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60H, 1P, 1A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 2A, C Charakteristik","A9F07102","10kA","Schneider",2,1.9,1.9,null,1.9,"LS-Schalter iC60H, 1P, 2A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 3A, C Charakteristik","A9F07103","10kA","Schneider",3,2.2000000000000002,2.2000000000000002,null,2.2000000000000002,"LS-Schalter iC60H, 1P, 3A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 4A, C Charakteristik","A9F07104","10kA","Schneider",4,2.4,2.4,null,2.4,"LS-Schalter iC60H, 1P, 4A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 6A, C Charakteristik","A9F07106","10kA","Schneider",6,1.3,1.3,null,1.3,"LS-Schalter iC60H, 1P, 6A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 10A, C Charakteristik","A9F07110","10kA","Schneider",10,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60H, 1P, 10A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 13A, C Charakteristik","A9F07113","10kA","Schneider",13,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60H, 1P, 13A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 16A, C Charakteristik","A9F07116","10kA","Schneider",16,2.4,2.4,null,2.4,"LS-Schalter iC60H, 1P, 16A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 20A, C Charakteristik","A9F07120","10kA","Schneider",20,2.4,2.4,null,2.4,"LS-Schalter iC60H, 1P, 20A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 25A, C Charakteristik","A9F07125","10kA","Schneider",25,3,3,null,3,"LS-Schalter iC60H, 1P, 25A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 32A, C Charakteristik","A9F07132","10kA","Schneider",32,2.8,2.8,null,2.8,"LS-Schalter iC60H, 1P, 32A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 40A, C Charakteristik","A9F07140","10kA","Schneider",40,3.6,3.6,null,3.6,"LS-Schalter iC60H, 1P, 40A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 50A, C Charakteristik","A9F07150","10kA","Schneider",50,4,4,null,4,"LS-Schalter iC60H, 1P, 50A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 63A, C Charakteristik","A9F07163","10kA","Schneider",63,5.6,5.6,null,5.6,"LS-Schalter iC60H, 1P, 63A, C Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  1P+N","Acti9","10kA","Schneider",null,null,null,null,0,"LS-Schalter  1P+N"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P+N, 1A, C Charakteristik","A9F07601","10kA","Schneider",1,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60H, 1P+N, 1A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P+N, 2A, C Charakteristik","A9F07602","10kA","Schneider",2,1.9,1.9,null,1.9,"LS-Schalter iC60H, 1P+N, 2A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P+N, 3A, C Charakteristik","A9F07603","10kA","Schneider",3,2.2000000000000002,2.2000000000000002,null,2.2000000000000002,"LS-Schalter iC60H, 1P+N, 3A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P+N, 4A, C Charakteristik","A9F07604","10kA","Schneider",4,2.4,2.4,null,2.4,"LS-Schalter iC60H, 1P+N, 4A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P+N, 6A, C Charakteristik","A9F07606","10kA","Schneider",6,1.3,1.3,null,1.3,"LS-Schalter iC60H, 1P+N, 6A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P+N, 10A, C Charakteristik","A9F07610","10kA","Schneider",10,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60H, 1P+N, 10A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P+N, 13A, C Charakteristik","A9F07613","10kA","Schneider",13,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60H, 1P+N, 13A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P+N, 16A, C Charakteristik","A9F07616","10kA","Schneider",16,2.4,2.4,null,{"$f":"G832+I832","v":2.4},"LS-Schalter iC60H, 1P+N, 16A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P+N, 20A, C Charakteristik","A9F07620","10kA","Schneider",20,2.4,2.4,null,2.4,"LS-Schalter iC60H, 1P+N, 20A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P+N, 25A, C Charakteristik","A9F07625","10kA","Schneider",25,3,3,null,3,"LS-Schalter iC60H, 1P+N, 25A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P+N, 32A, C Charakteristik","A9F07632","10kA","Schneider",32,2.8,2.8,null,2.8,"LS-Schalter iC60H, 1P+N, 32A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P+N, 40A, C Charakteristik","A9F07640","10kA","Schneider",40,3.6,3.6,null,3.6,"LS-Schalter iC60H, 1P+N, 40A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P+N, 50A, C Charakteristik","A9F07650","10kA","Schneider",50,4,4,null,4,"LS-Schalter iC60H, 1P+N, 50A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P+N, 63A, C Charakteristik","A9F07663","10kA","Schneider",63,5.6,5.6,null,5.6,"LS-Schalter iC60H, 1P+N, 63A, C Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  2P","Acti9","10kA","Schneider",null,null,null,null,0,"LS-Schalter  2P"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 1A, C Charakteristik","A9F07201","10kA","Schneider",1,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60H, 2P, 1A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 2A, C Charakteristik","A9F07202","10kA","Schneider",2,1.9,1.9,null,1.9,"LS-Schalter iC60H, 2P, 2A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 3A, C Charakteristik","A9F07203","10kA","Schneider",3,2.2000000000000002,2.2000000000000002,null,2.2000000000000002,"LS-Schalter iC60H, 2P, 3A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 4A, C Charakteristik","A9F07204","10kA","Schneider",4,2.4,2.4,null,2.4,"LS-Schalter iC60H, 2P, 4A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 6A, C Charakteristik","A9F07206","10kA","Schneider",6,1.3,1.3,null,1.3,"LS-Schalter iC60H, 2P, 6A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 10A, C Charakteristik","A9F07210","10kA","Schneider",10,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60H, 2P, 10A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 13A, C Charakteristik","A9F07213","10kA","Schneider",13,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60H, 2P, 13A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 16A, C Charakteristik","A9F07216","10kA","Schneider",16,2.4,2.4,null,2.4,"LS-Schalter iC60H, 2P, 16A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 20A, C Charakteristik","A9F07220","10kA","Schneider",20,2.4,2.4,null,2.4,"LS-Schalter iC60H, 2P, 20A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 25A, C Charakteristik","A9F07225","10kA","Schneider",25,3,3,null,3,"LS-Schalter iC60H, 2P, 25A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 32A, C Charakteristik","A9F07232","10kA","Schneider",32,2.8,2.8,null,2.8,"LS-Schalter iC60H, 2P, 32A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 40A, C Charakteristik","A9F07240","10kA","Schneider",40,3.6,3.6,null,3.6,"LS-Schalter iC60H, 2P, 40A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 50A, C Charakteristik","A9F07250","10kA","Schneider",50,4,4,null,4,"LS-Schalter iC60H, 2P, 50A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 63A, C Charakteristik","A9F07263","10kA","Schneider",63,5.6,5.6,null,5.6,"LS-Schalter iC60H, 2P, 63A, C Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  3P","Acti9","10kA","Schneider",null,null,null,null,0,"LS-Schalter  3P"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 1A, C Charakteristik","A9F07301","10kA","Schneider",1,2.2999999999999998,{"$f":"G857*3","v":6.8999999999999995},null,2.2999999999999998,"LS-Schalter iC60H, 3P, 1A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 2A, C Charakteristik","A9F07302","10kA","Schneider",2,1.9,{"$f":"G858*3","v":5.6999999999999993},null,1.9,"LS-Schalter iC60H, 3P, 2A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 3A, C Charakteristik","A9F07303","10kA","Schneider",3,2.2000000000000002,6.6000000000000005,null,2.2000000000000002,"LS-Schalter iC60H, 3P, 3A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 4A, C Charakteristik","A9F07304","10kA","Schneider",4,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60H, 3P, 4A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 6A, C Charakteristik","A9F07306","10kA","Schneider",6,1.3,3.9000000000000004,null,1.3,"LS-Schalter iC60H, 3P, 6A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 10A, C Charakteristik","A9F07310","10kA","Schneider",10,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60H, 3P, 10A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 13A, C Charakteristik","A9F07313","10kA","Schneider",13,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60H, 3P, 13A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 16A, C Charakteristik","A9F07316","10kA","Schneider",16,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60H, 3P, 16A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 20A, C Charakteristik","A9F07320","10kA","Schneider",20,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60H, 3P, 20A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 25A, C Charakteristik","A9F07325","10kA","Schneider",25,3,9,null,3,"LS-Schalter iC60H, 3P, 25A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 32A, C Charakteristik","A9F07332","10kA","Schneider",32,2.8,8.3999999999999986,null,2.8,"LS-Schalter iC60H, 3P, 32A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 40A, C Charakteristik","A9F07340","10kA","Schneider",40,3.6,10.8,null,3.6,"LS-Schalter iC60H, 3P, 40A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 50A, C Charakteristik","A9F07350","10kA","Schneider",50,4,12,null,4,"LS-Schalter iC60H, 3P, 50A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 63A, C Charakteristik","A9F07363","10kA","Schneider",63,5.6,16.799999999999997,null,5.6,"LS-Schalter iC60H, 3P, 63A, C Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  4P","Acti9","10kA","Schneider",null,null,null,null,0,"LS-Schalter  4P"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 1A, C Charakteristik","A9F07401","10kA","Schneider",1,2.2999999999999998,{"$f":"G873*3","v":6.8999999999999995},null,2.2999999999999998,"LS-Schalter iC60H, 4P, 1A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 2A, C Charakteristik","A9F07402","10kA","Schneider",2,1.9,{"$f":"G874*3","v":5.6999999999999993},null,1.9,"LS-Schalter iC60H, 4P, 2A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 3A, C Charakteristik","A9F07403","10kA","Schneider",3,2.2000000000000002,6.6000000000000005,null,2.2000000000000002,"LS-Schalter iC60H, 4P, 3A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 4A, C Charakteristik","A9F07404","10kA","Schneider",4,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60H, 4P, 4A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 6A, C Charakteristik","A9F07406","10kA","Schneider",6,1.3,3.9000000000000004,null,1.3,"LS-Schalter iC60H, 4P, 6A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 10A, C Charakteristik","A9F07410","10kA","Schneider",10,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60H, 4P, 10A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 13A, C Charakteristik","A9F07413","10kA","Schneider",13,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60H, 4P, 13A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 16A, C Charakteristik","A9F07416","10kA","Schneider",16,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60H, 4P, 16A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 20A, C Charakteristik","A9F07420","10kA","Schneider",20,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60H, 4P, 20A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 25A, C Charakteristik","A9F07425","10kA","Schneider",25,3,9,null,3,"LS-Schalter iC60H, 4P, 25A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 32A, C Charakteristik","A9F07432","10kA","Schneider",32,2.8,8.3999999999999986,null,2.8,"LS-Schalter iC60H, 4P, 32A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 40A, C Charakteristik","A9F07440","10kA","Schneider",40,3.6,10.8,null,3.6,"LS-Schalter iC60H, 4P, 40A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 50A, C Charakteristik","A9F07450","10kA","Schneider",50,4,12,null,4,"LS-Schalter iC60H, 4P, 50A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 63A, C Charakteristik","A9F07463","10kA","Schneider",63,5.6,16.799999999999997,null,5.6,"LS-Schalter iC60H, 4P, 63A, C Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  1P","Acti9","10kA","Schneider",null,null,null,null,0,"LS-Schalter  1P"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 1A, D Charakteristik","A9F08101","10kA","Schneider",1,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60H, 1P, 1A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 2A, D Charakteristik","A9F08102","10kA","Schneider",2,1.9,1.9,null,1.9,"LS-Schalter iC60H, 1P, 2A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 3A, D Charakteristik","A9F08103","10kA","Schneider",3,2.2000000000000002,2.2000000000000002,null,2.2000000000000002,"LS-Schalter iC60H, 1P, 3A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 4A, D Charakteristik","A9F08104","10kA","Schneider",4,2.4,2.4,null,2.4,"LS-Schalter iC60H, 1P, 4A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 6A, D Charakteristik","A9F08106","10kA","Schneider",6,1.3,1.3,null,1.3,"LS-Schalter iC60H, 1P, 6A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 10A, D Charakteristik","A9F08110","10kA","Schneider",10,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60H, 1P, 10A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 13A, D Charakteristik","A9F08113","10kA","Schneider",13,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60H, 1P, 13A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 16A, D Charakteristik","A9F08116","10kA","Schneider",16,2.4,2.4,null,{"$f":"G896+I896","v":2.4},"LS-Schalter iC60H, 1P, 16A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 20A, D Charakteristik","A9F08120","10kA","Schneider",20,2.4,2.4,null,2.4,"LS-Schalter iC60H, 1P, 20A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 25A, D Charakteristik","A9F08125","10kA","Schneider",25,3,3,null,3,"LS-Schalter iC60H, 1P, 25A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 32A, D Charakteristik","A9F08132","10kA","Schneider",32,2.8,2.8,null,2.8,"LS-Schalter iC60H, 1P, 32A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 40A, D Charakteristik","A9F08140","10kA","Schneider",40,3.6,3.6,null,3.6,"LS-Schalter iC60H, 1P, 40A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 50A, D Charakteristik","A9F08150","10kA","Schneider",50,4,4,null,4,"LS-Schalter iC60H, 1P, 50A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 1P, 63A, D Charakteristik","A9F08163","10kA","Schneider",63,5.6,5.6,null,5.6,"LS-Schalter iC60H, 1P, 63A, D Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  2P","Acti9","10kA","Schneider",null,null,null,null,0,"LS-Schalter  2P"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 1A, D Charakteristik","A9F08201","10kA","Schneider",1,2.2999999999999998,{"$f":"G905*2","v":4.5999999999999996},null,2.2999999999999998,"LS-Schalter iC60H, 2P, 1A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 2A, D Charakteristik","A9F08202","10kA","Schneider",2,1.9,{"$f":"G906*2","v":3.8},null,1.9,"LS-Schalter iC60H, 2P, 2A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 3A, D Charakteristik","A9F08203","10kA","Schneider",3,2.2000000000000002,4.4000000000000004,null,2.2000000000000002,"LS-Schalter iC60H, 2P, 3A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 4A, D Charakteristik","A9F08204","10kA","Schneider",4,2.4,4.8,null,2.4,"LS-Schalter iC60H, 2P, 4A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 6A, D Charakteristik","A9F08206","10kA","Schneider",6,1.3,2.6,null,1.3,"LS-Schalter iC60H, 2P, 6A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 10A, D Charakteristik","A9F08210","10kA","Schneider",10,2.2999999999999998,4.5999999999999996,null,2.2999999999999998,"LS-Schalter iC60H, 2P, 10A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 13A, D Charakteristik","A9F08213","10kA","Schneider",13,2.2999999999999998,4.5999999999999996,null,2.2999999999999998,"LS-Schalter iC60H, 2P, 13A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 16A, D Charakteristik","A9F08216","10kA","Schneider",16,2.4,4.8,null,2.4,"LS-Schalter iC60H, 2P, 16A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 20A, D Charakteristik","A9F08220","10kA","Schneider",20,2.4,4.8,null,2.4,"LS-Schalter iC60H, 2P, 20A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 25A, D Charakteristik","A9F08225","10kA","Schneider",25,3,6,null,3,"LS-Schalter iC60H, 2P, 25A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 32A, D Charakteristik","A9F08232","10kA","Schneider",32,2.8,5.6,null,2.8,"LS-Schalter iC60H, 2P, 32A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 40A, D Charakteristik","A9F08240","10kA","Schneider",40,3.6,7.2,null,3.6,"LS-Schalter iC60H, 2P, 40A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 50A, D Charakteristik","A9F08250","10kA","Schneider",50,4,8,null,4,"LS-Schalter iC60H, 2P, 50A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 2P, 63A, D Charakteristik","A9F08263","10kA","Schneider",63,5.6,11.2,null,5.6,"LS-Schalter iC60H, 2P, 63A, D Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  3P","Acti9","10kA","Schneider",null,null,null,null,0,"LS-Schalter  3P"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 1A, D Charakteristik","A9F08301","10kA","Schneider",1,2.2999999999999998,{"$f":"G921*3","v":6.8999999999999995},null,2.2999999999999998,"LS-Schalter iC60H, 3P, 1A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 2A, D Charakteristik","A9F08302","10kA","Schneider",2,1.9,{"$f":"G922*3","v":5.6999999999999993},null,1.9,"LS-Schalter iC60H, 3P, 2A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 3A, D Charakteristik","A9F08303","10kA","Schneider",3,2.2000000000000002,6.6000000000000005,null,2.2000000000000002,"LS-Schalter iC60H, 3P, 3A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 4A, D Charakteristik","A9F08304","10kA","Schneider",4,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60H, 3P, 4A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 6A, D Charakteristik","A9F08306","10kA","Schneider",6,1.3,3.9000000000000004,null,1.3,"LS-Schalter iC60H, 3P, 6A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 10A, D Charakteristik","A9F08310","10kA","Schneider",10,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60H, 3P, 10A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 13A, D Charakteristik","A9F08313","10kA","Schneider",13,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60H, 3P, 13A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 16A, D Charakteristik","A9F08316","10kA","Schneider",16,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60H, 3P, 16A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 20A, D Charakteristik","A9F08320","10kA","Schneider",20,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60H, 3P, 20A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 25A, D Charakteristik","A9F08325","10kA","Schneider",25,3,9,null,3,"LS-Schalter iC60H, 3P, 25A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 32A, D Charakteristik","A9F08332","10kA","Schneider",32,2.8,8.3999999999999986,null,2.8,"LS-Schalter iC60H, 3P, 32A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 40A, D Charakteristik","A9F08340","10kA","Schneider",40,3.6,10.8,null,3.6,"LS-Schalter iC60H, 3P, 40A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 50A, D Charakteristik","A9F08350","10kA","Schneider",50,4,12,null,4,"LS-Schalter iC60H, 3P, 50A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 3P, 63A, D Charakteristik","A9F08363","10kA","Schneider",63,5.6,16.799999999999997,null,5.6,"LS-Schalter iC60H, 3P, 63A, D Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  4P","Acti9","10kA","Schneider",null,null,null,null,0,"LS-Schalter  4P"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 1A, D Charakteristik","A9F08401","10kA","Schneider",1,2.2999999999999998,{"$f":"G937*3","v":6.8999999999999995},null,2.2999999999999998,"LS-Schalter iC60H, 4P, 1A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 2A, D Charakteristik","A9F08402","10kA","Schneider",2,1.9,{"$f":"G938*3","v":5.6999999999999993},null,1.9,"LS-Schalter iC60H, 4P, 2A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 3A, D Charakteristik","A9F08403","10kA","Schneider",3,2.2000000000000002,6.6000000000000005,null,2.2000000000000002,"LS-Schalter iC60H, 4P, 3A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 4A, D Charakteristik","A9F08404","10kA","Schneider",4,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60H, 4P, 4A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 6A, D Charakteristik","A9F08406","10kA","Schneider",6,1.3,3.9000000000000004,null,1.3,"LS-Schalter iC60H, 4P, 6A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 10A, D Charakteristik","A9F08410","10kA","Schneider",10,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60H, 4P, 10A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 13A, D Charakteristik","A9F08413","10kA","Schneider",13,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60H, 4P, 13A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 16A, D Charakteristik","A9F08416","10kA","Schneider",16,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60H, 4P, 16A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 20A, D Charakteristik","A9F08420","10kA","Schneider",20,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60H, 4P, 20A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 25A, D Charakteristik","A9F08425","10kA","Schneider",25,3,9,null,3,"LS-Schalter iC60H, 4P, 25A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 32A, D Charakteristik","A9F08432","10kA","Schneider",32,2.8,8.3999999999999986,null,2.8,"LS-Schalter iC60H, 4P, 32A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 40A, D Charakteristik","A9F08440","10kA","Schneider",40,3.6,10.8,null,3.6,"LS-Schalter iC60H, 4P, 40A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 50A, D Charakteristik","A9F08450","10kA","Schneider",50,4,12,null,4,"LS-Schalter iC60H, 4P, 50A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60H, 4P, 63A, D Charakteristik","A9F08463","10kA","Schneider",63,5.6,16.799999999999997,null,5.6,"LS-Schalter iC60H, 4P, 63A, D Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  1P","Acti9","6kA","Schneider",null,null,null,null,0,"LS-Schalter  1P"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 1A, B Charakteristik","A9F03101","6kA","Schneider",1,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60N, 1P, 1A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 2A, B Charakteristik","A9F03102","6kA","Schneider",2,1.9,1.9,null,1.9,"LS-Schalter iC60N, 1P, 2A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 4A, B Charakteristik","A9F03104","6kA","Schneider",4,2.4,2.4,null,2.4,"LS-Schalter iC60N, 1P, 4A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 6A, B Charakteristik","A9F03106","6kA","Schneider",6,1.3,1.3,null,1.3,"LS-Schalter iC60N, 1P, 6A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 10A, B Charakteristik","A9F03110","6kA","Schneider",10,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60N, 1P, 10A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 13A, B Charakteristik","A9F03113","6kA","Schneider",13,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60N, 1P, 13A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 16A, B Charakteristik","A9F03116","6kA","Schneider",16,2.4,2.4,null,2.4,"LS-Schalter iC60N, 1P, 16A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 20A, B Charakteristik","A9F03120","6kA","Schneider",20,2.4,2.4,null,{"$f":"G960+I960","v":2.4},"LS-Schalter iC60N, 1P, 20A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 25A, B Charakteristik","A9F03125","6kA","Schneider",25,3,3,null,3,"LS-Schalter iC60N, 1P, 25A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 32A, B Charakteristik","A9F03132","6kA","Schneider",32,2.8,2.8,null,2.8,"LS-Schalter iC60N, 1P, 32A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 40A, B Charakteristik","A9F03140","6kA","Schneider",40,3.6,3.6,null,3.6,"LS-Schalter iC60N, 1P, 40A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 50A, B Charakteristik","A9F03150","6kA","Schneider",50,4,4,null,4,"LS-Schalter iC60N, 1P, 50A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 63A, B Charakteristik","A9F03163","6kA","Schneider",63,5.6,5.6,null,5.6,"LS-Schalter iC60N, 1P, 63A, B Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  1P+N","Acti9","6kA","Schneider",null,null,null,null,0,"LS-Schalter  1P+N"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P+N, 6A, B Charakteristik","A9F03606","6kA","Schneider",6,1.3,1.3,null,1.3,"LS-Schalter iC60N, 1P+N, 6A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P+N, 10A, B Charakteristik","A9F03610","6kA","Schneider",10,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60N, 1P+N, 10A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P+N, 13A, B Charakteristik","A9F03613","6kA","Schneider",13,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60N, 1P+N, 13A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P+N, 16A, B Charakteristik","A9F03616","6kA","Schneider",16,2.4,2.4,null,2.4,"LS-Schalter iC60N, 1P+N, 16A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P+N, 20A, B Charakteristik","A9F03620","6kA","Schneider",20,2.4,2.4,null,2.4,"LS-Schalter iC60N, 1P+N, 20A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P+N, 25A, B Charakteristik","A9F03625","6kA","Schneider",25,3,3,null,3,"LS-Schalter iC60N, 1P+N, 25A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P+N, 32A, B Charakteristik","A9F03632","6kA","Schneider",32,2.8,2.8,null,2.8,"LS-Schalter iC60N, 1P+N, 32A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P+N, 40A, B Charakteristik","A9F03640","6kA","Schneider",40,3.6,3.6,null,3.6,"LS-Schalter iC60N, 1P+N, 40A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P+N, 50A, B Charakteristik","A9F03650","6kA","Schneider",50,4,4,null,4,"LS-Schalter iC60N, 1P+N, 50A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P+N, 63A, B Charakteristik","A9F03663","6kA","Schneider",63,5.6,5.6,null,5.6,"LS-Schalter iC60N, 1P+N, 63A, B Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  2P","Acti9","6kA","Schneider",null,null,null,null,0,"LS-Schalter  2P"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 2A, B Charakteristik","A9F03202","6kA","Schneider",2,1.9,{"$f":"2*G980","v":3.8},null,1.9,"LS-Schalter iC60N, 2P, 2A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 4A, B Charakteristik","A9F03204","6kA","Schneider",4,2.4,{"$f":"2*G981","v":4.8},null,2.4,"LS-Schalter iC60N, 2P, 4A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 6A, B Charakteristik","A9F03206","6kA","Schneider",6,1.3,2.6,null,1.3,"LS-Schalter iC60N, 2P, 6A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 10A, B Charakteristik","A9F03210","6kA","Schneider",10,2.2999999999999998,4.5999999999999996,null,2.2999999999999998,"LS-Schalter iC60N, 2P, 10A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 13A, B Charakteristik","A9F03213","6kA","Schneider",13,2.2999999999999998,4.5999999999999996,null,2.2999999999999998,"LS-Schalter iC60N, 2P, 13A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 16A, B Charakteristik","A9F03216","6kA","Schneider",16,2.4,4.8,null,2.4,"LS-Schalter iC60N, 2P, 16A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 20A, B Charakteristik","A9F03220","6kA","Schneider",20,2.4,4.8,null,2.4,"LS-Schalter iC60N, 2P, 20A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 25A, B Charakteristik","A9F03225","6kA","Schneider",25,3,6,null,3,"LS-Schalter iC60N, 2P, 25A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 32A, B Charakteristik","A9F03232","6kA","Schneider",32,2.8,5.6,null,2.8,"LS-Schalter iC60N, 2P, 32A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 40A, B Charakteristik","A9F03240","6kA","Schneider",40,3.6,7.2,null,3.6,"LS-Schalter iC60N, 2P, 40A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 50A, B Charakteristik","A9F03250","6kA","Schneider",50,4,8,null,4,"LS-Schalter iC60N, 2P, 50A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 63A, B Charakteristik","A9F03263","6kA","Schneider",63,5.6,11.2,null,5.6,"LS-Schalter iC60N, 2P, 63A, B Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  3P","Acti9","6kA","Schneider",null,null,null,null,0,"LS-Schalter  3P"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 2A, B Charakteristik","A9F03302","6kA","Schneider",2,1.9,{"$f":"3*G994","v":5.6999999999999993},null,1.9,"LS-Schalter iC60N, 3P, 2A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 6A, B Charakteristik","A9F03306","6kA","Schneider",6,1.3,{"$f":"3*G995","v":3.9000000000000004},null,1.3,"LS-Schalter iC60N, 3P, 6A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 10A, B Charakteristik","A9F03310","6kA","Schneider",10,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60N, 3P, 10A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 13A, B Charakteristik","A9F03313","6kA","Schneider",13,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60N, 3P, 13A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 16A, B Charakteristik","A9F03316","6kA","Schneider",16,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60N, 3P, 16A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 20A, B Charakteristik","A9F03320","6kA","Schneider",20,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60N, 3P, 20A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 25A, B Charakteristik","A9F03325","6kA","Schneider",25,3,9,null,3,"LS-Schalter iC60N, 3P, 25A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 32A, B Charakteristik","A9F03332","6kA","Schneider",32,2.8,8.3999999999999986,null,2.8,"LS-Schalter iC60N, 3P, 32A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 40A, B Charakteristik","A9F03340","6kA","Schneider",40,3.6,10.8,null,3.6,"LS-Schalter iC60N, 3P, 40A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 50A, B Charakteristik","A9F03350","6kA","Schneider",50,4,12,null,4,"LS-Schalter iC60N, 3P, 50A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 63A, B Charakteristik","A9F03363","6kA","Schneider",63,5.6,16.799999999999997,null,5.6,"LS-Schalter iC60N, 3P, 63A, B Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  3P+N","Acti9","6kA","Schneider",null,null,null,null,0,"LS-Schalter  3P+N"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P+N, 6A, B Charakteristik","A9F03706","6kA","Schneider",6,1.3,{"$f":"3*G1007","v":3.9000000000000004},null,1.3,"LS-Schalter iC60N, 3P+N, 6A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P+N, 10A, B Charakteristik","A9F03710","6kA","Schneider",10,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60N, 3P+N, 10A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P+N, 13A, B Charakteristik","A9F03713","6kA","Schneider",13,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60N, 3P+N, 13A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P+N, 16A, B Charakteristik","A9F03716","6kA","Schneider",16,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60N, 3P+N, 16A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P+N, 20A, B Charakteristik","A9F03720","6kA","Schneider",20,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60N, 3P+N, 20A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P+N, 25A, B Charakteristik","A9F03725","6kA","Schneider",25,3,9,null,3,"LS-Schalter iC60N, 3P+N, 25A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P+N, 32A, B Charakteristik","A9F03732","6kA","Schneider",32,2.8,8.3999999999999986,null,2.8,"LS-Schalter iC60N, 3P+N, 32A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P+N, 40A, B Charakteristik","A9F03740","6kA","Schneider",40,3.6,10.8,null,3.6,"LS-Schalter iC60N, 3P+N, 40A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P+N, 50A, B Charakteristik","A9F03750","6kA","Schneider",50,4,12,null,4,"LS-Schalter iC60N, 3P+N, 50A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P+N, 63A, B Charakteristik","A9F03763","6kA","Schneider",63,5.6,16.799999999999997,null,5.6,"LS-Schalter iC60N, 3P+N, 63A, B Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  4P","Acti9","6kA","Schneider",null,null,null,null,0,"LS-Schalter  4P"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 6A, B Charakteristik","A9F03406","6kA","Schneider",6,1.3,{"$f":"3*G1019","v":3.9000000000000004},null,1.3,"LS-Schalter iC60N, 4P, 6A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 10A, B Charakteristik","A9F03410","6kA","Schneider",10,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60N, 4P, 10A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 13A, B Charakteristik","A9F03413","6kA","Schneider",13,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60N, 4P, 13A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 16A, B Charakteristik","A9F03416","6kA","Schneider",16,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60N, 4P, 16A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 20A, B Charakteristik","A9F03420","6kA","Schneider",20,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60N, 4P, 20A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 25A, B Charakteristik","A9F03425","6kA","Schneider",25,3,9,null,{"$f":"G1024+I1024","v":3},"LS-Schalter iC60N, 4P, 25A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 32A, B Charakteristik","A9F03432","6kA","Schneider",32,2.8,8.3999999999999986,null,2.8,"LS-Schalter iC60N, 4P, 32A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 40A, B Charakteristik","A9F03440","6kA","Schneider",40,3.6,10.8,null,3.6,"LS-Schalter iC60N, 4P, 40A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 50A, B Charakteristik","A9F03450","6kA","Schneider",50,4,12,null,4,"LS-Schalter iC60N, 4P, 50A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 63A, B Charakteristik","A9F03463","6kA","Schneider",63,5.6,16.799999999999997,null,5.6,"LS-Schalter iC60N, 4P, 63A, B Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  1P","Acti9","6kA","Schneider",null,null,null,null,0,"LS-Schalter  1P"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 1A, C Charakteristik","A9F04101","6kA","Schneider",1,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60N, 1P, 1A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 2A, C Charakteristik","A9F04102","6kA","Schneider",2,1.9,1.9,null,1.9,"LS-Schalter iC60N, 1P, 2A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 3A, C Charakteristik","A9F04103","6kA","Schneider",3,2.2000000000000002,2.2000000000000002,null,2.2000000000000002,"LS-Schalter iC60N, 1P, 3A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 4A, C Charakteristik","A9F04104","6kA","Schneider",4,2.4,2.4,null,2.4,"LS-Schalter iC60N, 1P, 4A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 6A, C Charakteristik","A9F04106","6kA","Schneider",6,1.3,1.3,null,1.3,"LS-Schalter iC60N, 1P, 6A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 10A, C Charakteristik","A9F04110","6kA","Schneider",10,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60N, 1P, 10A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 13A, C Charakteristik","A9F04113","6kA","Schneider",13,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60N, 1P, 13A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 16A, C Charakteristik","A9F04116","6kA","Schneider",16,2.4,2.4,null,2.4,"LS-Schalter iC60N, 1P, 16A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 20A, C Charakteristik","A9F04120","6kA","Schneider",20,2.4,2.4,null,2.4,"LS-Schalter iC60N, 1P, 20A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 25A, C Charakteristik","A9F04125","6kA","Schneider",25,3,3,null,3,"LS-Schalter iC60N, 1P, 25A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 32A, C Charakteristik","A9F04132","6kA","Schneider",32,2.8,2.8,null,2.8,"LS-Schalter iC60N, 1P, 32A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 40A, C Charakteristik","A9F04140","6kA","Schneider",40,3.6,3.6,null,3.6,"LS-Schalter iC60N, 1P, 40A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 50A, C Charakteristik","A9F04150","6kA","Schneider",50,4,4,null,4,"LS-Schalter iC60N, 1P, 50A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 63A, C Charakteristik","A9F04163","6kA","Schneider",63,5.6,5.6,null,5.6,"LS-Schalter iC60N, 1P, 63A, C Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  1P+N","Acti9","6kA","Schneider",null,null,null,null,0,"LS-Schalter  1P+N"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P+N, 1A, C Charakteristik","A9F04601","6kA","Schneider",1,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60N, 1P+N, 1A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P+N, 2A, C Charakteristik","A9F04602","6kA","Schneider",2,1.9,1.9,null,1.9,"LS-Schalter iC60N, 1P+N, 2A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P+N, 3A, C Charakteristik","A9F04603","6kA","Schneider",3,2.2000000000000002,2.2000000000000002,null,2.2000000000000002,"LS-Schalter iC60N, 1P+N, 3A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P+N, 4A, C Charakteristik","A9F04604","6kA","Schneider",4,2.4,2.4,null,2.4,"LS-Schalter iC60N, 1P+N, 4A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P+N, 6A, C Charakteristik","A9F04606","6kA","Schneider",6,1.3,1.3,null,1.3,"LS-Schalter iC60N, 1P+N, 6A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P+N, 10A, C Charakteristik","A9F04610","6kA","Schneider",10,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60N, 1P+N, 10A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P+N, 13A, C Charakteristik","A9F04613","6kA","Schneider",13,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60N, 1P+N, 13A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P+N, 16A, C Charakteristik","A9F04616","6kA","Schneider",16,2.4,2.4,null,2.4,"LS-Schalter iC60N, 1P+N, 16A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P+N, 20A, C Charakteristik","A9F04620","6kA","Schneider",20,2.4,2.4,null,2.4,"LS-Schalter iC60N, 1P+N, 20A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P+N, 25A, C Charakteristik","A9F04625","6kA","Schneider",25,3,3,null,3,"LS-Schalter iC60N, 1P+N, 25A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P+N, 32A, C Charakteristik","A9F04632","6kA","Schneider",32,2.8,2.8,null,2.8,"LS-Schalter iC60N, 1P+N, 32A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P+N, 40A, C Charakteristik","A9F04640","6kA","Schneider",40,3.6,3.6,null,3.6,"LS-Schalter iC60N, 1P+N, 40A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P+N, 50A, C Charakteristik","A9F04650","6kA","Schneider",50,4,4,null,4,"LS-Schalter iC60N, 1P+N, 50A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P+N, 63A, C Charakteristik","A9F04663","6kA","Schneider",63,5.6,5.6,null,5.6,"LS-Schalter iC60N, 1P+N, 63A, C Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  2P","Acti9","6kA","Schneider",null,null,null,null,0,"LS-Schalter  2P"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 1A, C Charakteristik","A9F04201","6kA","Schneider",1,2.2999999999999998,{"$f":"2*G1063","v":4.5999999999999996},null,2.2999999999999998,"LS-Schalter iC60N, 2P, 1A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 2A, C Charakteristik","A9F04202","6kA","Schneider",2,1.9,{"$f":"2*G1064","v":3.8},null,1.9,"LS-Schalter iC60N, 2P, 2A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 3A, C Charakteristik","A9F04203","6kA","Schneider",3,2.2000000000000002,4.4000000000000004,null,2.2000000000000002,"LS-Schalter iC60N, 2P, 3A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 4A, C Charakteristik","A9F04204","6kA","Schneider",4,2.4,4.8,null,2.4,"LS-Schalter iC60N, 2P, 4A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 6A, C Charakteristik","A9F04206","6kA","Schneider",6,1.3,2.6,null,1.3,"LS-Schalter iC60N, 2P, 6A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 10A, C Charakteristik","A9F04210","6kA","Schneider",10,2.2999999999999998,4.5999999999999996,null,2.2999999999999998,"LS-Schalter iC60N, 2P, 10A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 13A, C Charakteristik","A9F04213","6kA","Schneider",13,2.2999999999999998,4.5999999999999996,null,2.2999999999999998,"LS-Schalter iC60N, 2P, 13A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 16A, C Charakteristik","A9F04216","6kA","Schneider",16,2.4,4.8,null,2.4,"LS-Schalter iC60N, 2P, 16A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 20A, C Charakteristik","A9F04220","6kA","Schneider",20,2.4,4.8,null,2.4,"LS-Schalter iC60N, 2P, 20A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 25A, C Charakteristik","A9F04225","6kA","Schneider",25,3,6,null,3,"LS-Schalter iC60N, 2P, 25A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 32A, C Charakteristik","A9F04232","6kA","Schneider",32,2.8,5.6,null,2.8,"LS-Schalter iC60N, 2P, 32A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 40A, C Charakteristik","A9F04240","6kA","Schneider",40,3.6,7.2,null,3.6,"LS-Schalter iC60N, 2P, 40A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 50A, C Charakteristik","A9F04250","6kA","Schneider",50,4,8,null,4,"LS-Schalter iC60N, 2P, 50A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 63A, C Charakteristik","A9F04263","6kA","Schneider",63,5.6,11.2,null,5.6,"LS-Schalter iC60N, 2P, 63A, C Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  3P","Acti9","6kA","Schneider",null,null,null,null,0,"LS-Schalter  3P"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 1A, C Charakteristik","A9F04301","6kA","Schneider",1,2.2999999999999998,{"$f":"3*G1079","v":6.8999999999999995},null,2.2999999999999998,"LS-Schalter iC60N, 3P, 1A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 2A, C Charakteristik","A9F04302","6kA","Schneider",2,1.9,{"$f":"3*G1080","v":5.6999999999999993},null,1.9,"LS-Schalter iC60N, 3P, 2A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 3A, C Charakteristik","A9F04303","6kA","Schneider",3,2.2000000000000002,6.6000000000000005,null,2.2000000000000002,"LS-Schalter iC60N, 3P, 3A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 4A, C Charakteristik","A9F04304","6kA","Schneider",4,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60N, 3P, 4A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 6A, C Charakteristik","A9F04306","6kA","Schneider",6,1.3,3.9000000000000004,null,1.3,"LS-Schalter iC60N, 3P, 6A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 10A, C Charakteristik","A9F04310","6kA","Schneider",10,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60N, 3P, 10A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 13A, C Charakteristik","A9F04313","6kA","Schneider",13,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60N, 3P, 13A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 16A, C Charakteristik","A9F04316","6kA","Schneider",16,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60N, 3P, 16A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 20A, C Charakteristik","A9F04320","6kA","Schneider",20,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60N, 3P, 20A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 25A, C Charakteristik","A9F04325","6kA","Schneider",25,3,9,null,{"$f":"G1088+I1088","v":3},"LS-Schalter iC60N, 3P, 25A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 32A, C Charakteristik","A9F04332","6kA","Schneider",32,2.8,8.3999999999999986,null,2.8,"LS-Schalter iC60N, 3P, 32A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 40A, C Charakteristik","A9F04340","6kA","Schneider",40,3.6,10.8,null,3.6,"LS-Schalter iC60N, 3P, 40A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 50A, C Charakteristik","A9F04350","6kA","Schneider",50,4,12,null,4,"LS-Schalter iC60N, 3P, 50A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 63A, C Charakteristik","A9F04363","6kA","Schneider",63,5.6,16.799999999999997,null,5.6,"LS-Schalter iC60N, 3P, 63A, C Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  3P+N","Acti9","6kA","Schneider",null,null,null,null,0,"LS-Schalter  3P+N"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P+N, 1A, C Charakteristik","A9F04701","6kA","Schneider",1,2.2999999999999998,{"$f":"3*G1095","v":6.8999999999999995},null,2.2999999999999998,"LS-Schalter iC60N, 3P+N, 1A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P+N, 2A, C Charakteristik","A9F04702","6kA","Schneider",2,1.9,{"$f":"3*G1096","v":5.6999999999999993},null,1.9,"LS-Schalter iC60N, 3P+N, 2A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P+N, 3A, C Charakteristik","A9F04703","6kA","Schneider",3,2.2000000000000002,6.6000000000000005,null,2.2000000000000002,"LS-Schalter iC60N, 3P+N, 3A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P+N, 4A, C Charakteristik","A9F04704","6kA","Schneider",4,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60N, 3P+N, 4A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P+N, 6A, C Charakteristik","A9F04706","6kA","Schneider",6,1.3,3.9000000000000004,null,1.3,"LS-Schalter iC60N, 3P+N, 6A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P+N, 10A, C Charakteristik","A9F04710","6kA","Schneider",10,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60N, 3P+N, 10A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P+N, 13A, C Charakteristik","A9F04713","6kA","Schneider",13,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60N, 3P+N, 13A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P+N, 16A, C Charakteristik","A9F04716","6kA","Schneider",16,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60N, 3P+N, 16A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P+N, 20A, C Charakteristik","A9F04720","6kA","Schneider",20,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60N, 3P+N, 20A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P+N, 25A, C Charakteristik","A9F04725","6kA","Schneider",25,3,9,null,3,"LS-Schalter iC60N, 3P+N, 25A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P+N, 32A, C Charakteristik","A9F04732","6kA","Schneider",32,2.8,8.3999999999999986,null,2.8,"LS-Schalter iC60N, 3P+N, 32A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P+N, 40A, C Charakteristik","A9F04740","6kA","Schneider",40,3.6,10.8,null,3.6,"LS-Schalter iC60N, 3P+N, 40A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P+N, 50A, C Charakteristik","A9F04750","6kA","Schneider",50,4,12,null,4,"LS-Schalter iC60N, 3P+N, 50A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P+N, 63A, C Charakteristik","A9F04763","6kA","Schneider",63,5.6,16.799999999999997,null,5.6,"LS-Schalter iC60N, 3P+N, 63A, C Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  4P","Acti9","6kA","Schneider",null,null,null,null,0,"LS-Schalter  4P"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 1A, C Charakteristik","A9F04401","6kA","Schneider",1,2.2999999999999998,{"$f":"3*G1111","v":6.8999999999999995},null,2.2999999999999998,"LS-Schalter iC60N, 4P, 1A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 2A, C Charakteristik","A9F04402","6kA","Schneider",2,1.9,{"$f":"3*G1112","v":5.6999999999999993},null,1.9,"LS-Schalter iC60N, 4P, 2A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 3A, C Charakteristik","A9F04403","6kA","Schneider",3,2.2000000000000002,6.6000000000000005,null,2.2000000000000002,"LS-Schalter iC60N, 4P, 3A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 4A, C Charakteristik","A9F04404","6kA","Schneider",4,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60N, 4P, 4A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 6A, C Charakteristik","A9F04406","6kA","Schneider",6,1.3,3.9000000000000004,null,1.3,"LS-Schalter iC60N, 4P, 6A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 10A, C Charakteristik","A9F04410","6kA","Schneider",10,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60N, 4P, 10A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 13A, C Charakteristik","A9F04413","6kA","Schneider",13,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60N, 4P, 13A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 16A, C Charakteristik","A9F04416","6kA","Schneider",16,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60N, 4P, 16A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 20A, C Charakteristik","A9F04420","6kA","Schneider",20,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60N, 4P, 20A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 25A, C Charakteristik","A9F04425","6kA","Schneider",25,3,9,null,3,"LS-Schalter iC60N, 4P, 25A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 32A, C Charakteristik","A9F04432","6kA","Schneider",32,2.8,8.3999999999999986,null,2.8,"LS-Schalter iC60N, 4P, 32A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 40A, C Charakteristik","A9F04440","6kA","Schneider",40,3.6,10.8,null,3.6,"LS-Schalter iC60N, 4P, 40A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 50A, C Charakteristik","A9F04450","6kA","Schneider",50,4,12,null,4,"LS-Schalter iC60N, 4P, 50A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 63A, C Charakteristik","A9F04463","6kA","Schneider",63,5.6,16.799999999999997,null,5.6,"LS-Schalter iC60N, 4P, 63A, C Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  1P","Acti9","6kA","Schneider",null,null,null,null,0,"LS-Schalter  1P"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 1A, D Charakteristik","A9F05101","6kA","Schneider",1,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60N, 1P, 1A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 2A, D Charakteristik","A9F05102","6kA","Schneider",2,1.9,1.9,null,1.9,"LS-Schalter iC60N, 1P, 2A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 3A, D Charakteristik","A9F05103","6kA","Schneider",3,2.2000000000000002,2.2000000000000002,null,2.2000000000000002,"LS-Schalter iC60N, 1P, 3A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 4A, D Charakteristik","A9F05104","6kA","Schneider",4,2.4,2.4,null,2.4,"LS-Schalter iC60N, 1P, 4A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 6A, D Charakteristik","A9F05106","6kA","Schneider",6,1.3,1.3,null,1.3,"LS-Schalter iC60N, 1P, 6A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 10A, D Charakteristik","A9F05110","6kA","Schneider",10,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60N, 1P, 10A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 13A, D Charakteristik","A9F05113","6kA","Schneider",13,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60N, 1P, 13A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 16A, D Charakteristik","A9F05116","6kA","Schneider",16,2.4,2.4,null,2.4,"LS-Schalter iC60N, 1P, 16A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 20A, D Charakteristik","A9F05120","6kA","Schneider",20,2.4,2.4,null,2.4,"LS-Schalter iC60N, 1P, 20A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 25A, D Charakteristik","A9F05125","6kA","Schneider",25,3,3,null,3,"LS-Schalter iC60N, 1P, 25A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 32A, D Charakteristik","A9F05132","6kA","Schneider",32,2.8,2.8,null,2.8,"LS-Schalter iC60N, 1P, 32A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 40A, D Charakteristik","A9F05140","6kA","Schneider",40,3.6,3.6,null,3.6,"LS-Schalter iC60N, 1P, 40A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 50A, D Charakteristik","A9F05150","6kA","Schneider",50,4,4,null,4,"LS-Schalter iC60N, 1P, 50A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 1P, 63A, D Charakteristik","A9F05163","6kA","Schneider",63,5.6,5.6,null,5.6,"LS-Schalter iC60N, 1P, 63A, D Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  2P","Acti9","6kA","Schneider",null,null,null,null,0,"LS-Schalter  2P"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 1A, D Charakteristik","A9F05201","6kA","Schneider",1,2.2999999999999998,{"$f":"2*G1143","v":4.5999999999999996},null,2.2999999999999998,"LS-Schalter iC60N, 2P, 1A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 2A, D Charakteristik","A9F05202","6kA","Schneider",2,1.9,{"$f":"2*G1144","v":3.8},null,1.9,"LS-Schalter iC60N, 2P, 2A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 3A, D Charakteristik","A9F05203","6kA","Schneider",3,2.2000000000000002,4.4000000000000004,null,2.2000000000000002,"LS-Schalter iC60N, 2P, 3A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 4A, D Charakteristik","A9F05204","6kA","Schneider",4,2.4,4.8,null,2.4,"LS-Schalter iC60N, 2P, 4A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 6A, D Charakteristik","A9F05206","6kA","Schneider",6,1.3,2.6,null,1.3,"LS-Schalter iC60N, 2P, 6A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 10A, D Charakteristik","A9F05210","6kA","Schneider",10,2.2999999999999998,4.5999999999999996,null,2.2999999999999998,"LS-Schalter iC60N, 2P, 10A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 13A, D Charakteristik","A9F05213","6kA","Schneider",13,2.2999999999999998,4.5999999999999996,null,2.2999999999999998,"LS-Schalter iC60N, 2P, 13A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 16A, D Charakteristik","A9F05216","6kA","Schneider",16,2.4,4.8,null,2.4,"LS-Schalter iC60N, 2P, 16A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 20A, D Charakteristik","A9F05220","6kA","Schneider",20,2.4,4.8,null,2.4,"LS-Schalter iC60N, 2P, 20A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 25A, D Charakteristik","A9F05225","6kA","Schneider",25,3,6,null,{"$f":"G1152+I1152","v":3},"LS-Schalter iC60N, 2P, 25A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 32A, D Charakteristik","A9F05232","6kA","Schneider",32,2.8,5.6,null,2.8,"LS-Schalter iC60N, 2P, 32A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 40A, D Charakteristik","A9F05240","6kA","Schneider",40,3.6,7.2,null,3.6,"LS-Schalter iC60N, 2P, 40A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 50A, D Charakteristik","A9F05250","6kA","Schneider",50,4,8,null,4,"LS-Schalter iC60N, 2P, 50A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 2P, 63A, D Charakteristik","A9F05263","6kA","Schneider",63,5.6,11.2,null,5.6,"LS-Schalter iC60N, 2P, 63A, D Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  3P","Acti9","6kA","Schneider",null,null,null,null,0,"LS-Schalter  3P"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 1A, D Charakteristik","A9F05301","6kA","Schneider",1,2.2999999999999998,{"$f":"G1159*3","v":6.8999999999999995},null,2.2999999999999998,"LS-Schalter iC60N, 3P, 1A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 2A, D Charakteristik","A9F05302","6kA","Schneider",2,1.9,{"$f":"G1160*3","v":5.6999999999999993},null,1.9,"LS-Schalter iC60N, 3P, 2A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 3A, D Charakteristik","A9F05303","6kA","Schneider",3,2.2000000000000002,6.6000000000000005,null,2.2000000000000002,"LS-Schalter iC60N, 3P, 3A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 4A, D Charakteristik","A9F05304","6kA","Schneider",4,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60N, 3P, 4A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 6A, D Charakteristik","A9F05306","6kA","Schneider",6,1.3,3.9000000000000004,null,1.3,"LS-Schalter iC60N, 3P, 6A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 10A, D Charakteristik","A9F05310","6kA","Schneider",10,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60N, 3P, 10A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 13A, D Charakteristik","A9F05313","6kA","Schneider",13,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60N, 3P, 13A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 16A, D Charakteristik","A9F05316","6kA","Schneider",16,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60N, 3P, 16A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 20A, D Charakteristik","A9F05320","6kA","Schneider",20,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60N, 3P, 20A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 25A, D Charakteristik","A9F05325","6kA","Schneider",25,3,9,null,3,"LS-Schalter iC60N, 3P, 25A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 32A, D Charakteristik","A9F05332","6kA","Schneider",32,2.8,8.3999999999999986,null,2.8,"LS-Schalter iC60N, 3P, 32A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 40A, D Charakteristik","A9F05340","6kA","Schneider",40,3.6,10.8,null,3.6,"LS-Schalter iC60N, 3P, 40A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 50A, D Charakteristik","A9F05350","6kA","Schneider",50,4,12,null,4,"LS-Schalter iC60N, 3P, 50A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 3P, 63A, D Charakteristik","A9F05363","6kA","Schneider",63,5.6,16.799999999999997,null,5.6,"LS-Schalter iC60N, 3P, 63A, D Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  4P","Acti9","6kA","Schneider",null,null,null,null,0,"LS-Schalter  4P"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 1A, D Charakteristik","A9F05401","6kA","Schneider",1,2.2999999999999998,{"$f":"G1175*3","v":6.8999999999999995},null,2.2999999999999998,"LS-Schalter iC60N, 4P, 1A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 2A, D Charakteristik","A9F05402","6kA","Schneider",2,1.9,{"$f":"G1176*3","v":5.6999999999999993},null,1.9,"LS-Schalter iC60N, 4P, 2A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 3A, D Charakteristik","A9F05403","6kA","Schneider",3,2.2000000000000002,6.6000000000000005,null,2.2000000000000002,"LS-Schalter iC60N, 4P, 3A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 4A, D Charakteristik","A9F05404","6kA","Schneider",4,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60N, 4P, 4A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 6A, D Charakteristik","A9F05406","6kA","Schneider",6,1.3,3.9000000000000004,null,1.3,"LS-Schalter iC60N, 4P, 6A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 10A, D Charakteristik","A9F05410","6kA","Schneider",10,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60N, 4P, 10A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 13A, D Charakteristik","A9F05413","6kA","Schneider",13,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60N, 4P, 13A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 16A, D Charakteristik","A9F05416","6kA","Schneider",16,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60N, 4P, 16A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 20A, D Charakteristik","A9F05420","6kA","Schneider",20,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60N, 4P, 20A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 25A, D Charakteristik","A9F05425","6kA","Schneider",25,3,9,null,3,"LS-Schalter iC60N, 4P, 25A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 32A, D Charakteristik","A9F05432","6kA","Schneider",32,2.8,8.3999999999999986,null,2.8,"LS-Schalter iC60N, 4P, 32A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 40A, D Charakteristik","A9F05440","6kA","Schneider",40,3.6,10.8,null,3.6,"LS-Schalter iC60N, 4P, 40A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 50A, D Charakteristik","A9F05450","6kA","Schneider",50,4,12,null,4,"LS-Schalter iC60N, 4P, 50A, D Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60N, 4P, 63A, D Charakteristik","A9F05463","6kA","Schneider",63,5.6,16.799999999999997,null,5.6,"LS-Schalter iC60N, 4P, 63A, D Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  1P","Acti9",null,"Schneider",null,null,null,null,0,"LS-Schalter  1P"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 1A, B Charakteristik","A9F93101","100kA","Schneider",1,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60L, 1P, 1A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 2A, B Charakteristik","A9F93102","100kA","Schneider",2,1.9,1.9,null,1.9,"LS-Schalter iC60L, 1P, 2A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 4A, B Charakteristik","A9F93104","100kA","Schneider",4,2.4,2.4,null,2.4,"LS-Schalter iC60L, 1P, 4A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 6A, B Charakteristik","A9F93106","25kA","Schneider",6,1.3,1.3,null,1.3,"LS-Schalter iC60L, 1P, 6A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 10A, B Charakteristik","A9F93110","25kA","Schneider",10,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60L, 1P, 10A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 13A, B Charakteristik","A9F93113","25kA","Schneider",13,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60L, 1P, 13A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 16A, B Charakteristik","A9F93116","25kA","Schneider",16,2.4,2.4,null,2.4,"LS-Schalter iC60L, 1P, 16A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 20A, B Charakteristik","A9F93120","25kA","Schneider",20,2.4,2.4,null,2.4,"LS-Schalter iC60L, 1P, 20A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 25A, B Charakteristik","A9F93125","25kA","Schneider",25,3,3,null,3,"LS-Schalter iC60L, 1P, 25A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 32A, B Charakteristik","A9F93132","20kA","Schneider",32,2.8,2.8,null,2.8,"LS-Schalter iC60L, 1P, 32A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 40A, B Charakteristik","A9F93140","20kA","Schneider",40,3.6,3.6,null,3.6,"LS-Schalter iC60L, 1P, 40A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 50A, B Charakteristik","A9F93150","15kA","Schneider",50,4,4,null,4,"LS-Schalter iC60L, 1P, 50A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 63A, B Charakteristik","A9F93163","15kA","Schneider",63,5.6,5.6,null,5.6,"LS-Schalter iC60L, 1P, 63A, B Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  1P+N","Acti9",null,"Schneider",null,null,null,null,0,"LS-Schalter  1P+N"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P+N, 6A, B Charakteristik","A9F93606","25kA","Schneider",6,1.3,1.3,null,1.3,"LS-Schalter iC60L, 1P+N, 6A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P+N, 10A, B Charakteristik","A9F93610","25kA","Schneider",10,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60L, 1P+N, 10A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P+N, 13A, B Charakteristik","A9F93613","25kA","Schneider",13,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60L, 1P+N, 13A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P+N, 16A, B Charakteristik","A9F93616","25kA","Schneider",16,2.4,2.4,null,2.4,"LS-Schalter iC60L, 1P+N, 16A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P+N, 20A, B Charakteristik","A9F93620","25kA","Schneider",20,2.4,2.4,null,2.4,"LS-Schalter iC60L, 1P+N, 20A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P+N, 25A, B Charakteristik","A9F93625","25kA","Schneider",25,3,3,null,3,"LS-Schalter iC60L, 1P+N, 25A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P+N, 32A, B Charakteristik","A9F93632","20kA","Schneider",32,2.8,2.8,null,2.8,"LS-Schalter iC60L, 1P+N, 32A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P+N, 40A, B Charakteristik","A9F93640","20kA","Schneider",40,3.6,3.6,null,3.6,"LS-Schalter iC60L, 1P+N, 40A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P+N, 50A, B Charakteristik","A9F93650","15kA","Schneider",50,4,4,null,4,"LS-Schalter iC60L, 1P+N, 50A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P+N, 63A, B Charakteristik","A9F93663","15kA","Schneider",63,5.6,5.6,null,5.6,"LS-Schalter iC60L, 1P+N, 63A, B Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,{"$f":"G1216+I1216","v":0}]
["Leistungsschalter REG","LS-Schalter  2P","Acti9","20kA","Schneider",null,null,null,null,0,"LS-Schalter  2P"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 2A, B Charakteristik","A9F93202","100kA","Schneider",2,1.9,{"$f":"2*G1218","v":3.8},null,1.9,"LS-Schalter iC60L, 2P, 2A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 4A, B Charakteristik","A9F93204","100kA","Schneider",4,2.4,{"$f":"2*G1219","v":4.8},null,2.4,"LS-Schalter iC60L, 2P, 4A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 6A, B Charakteristik","A9F93206","25kA","Schneider",6,1.3,2.6,null,1.3,"LS-Schalter iC60L, 2P, 6A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 10A, B Charakteristik","A9F93210","25kA","Schneider",10,2.2999999999999998,4.5999999999999996,null,2.2999999999999998,"LS-Schalter iC60L, 2P, 10A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 13A, B Charakteristik","A9F93213","25kA","Schneider",13,2.2999999999999998,4.5999999999999996,null,2.2999999999999998,"LS-Schalter iC60L, 2P, 13A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 16A, B Charakteristik","A9F93216","25kA","Schneider",16,2.4,4.8,null,2.4,"LS-Schalter iC60L, 2P, 16A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 20A, B Charakteristik","A9F93220","25kA","Schneider",20,2.4,4.8,null,2.4,"LS-Schalter iC60L, 2P, 20A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 25A, B Charakteristik","A9F93225","25kA","Schneider",25,3,6,null,3,"LS-Schalter iC60L, 2P, 25A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 32A, B Charakteristik","A9F93232","20kA","Schneider",32,2.8,5.6,null,2.8,"LS-Schalter iC60L, 2P, 32A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 40A, B Charakteristik","A9F93240","20kA","Schneider",40,3.6,7.2,null,3.6,"LS-Schalter iC60L, 2P, 40A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 50A, B Charakteristik","A9F93250","15kA","Schneider",50,4,8,null,4,"LS-Schalter iC60L, 2P, 50A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 63A, B Charakteristik","A9F93263","15kA","Schneider",63,5.6,11.2,null,5.6,"LS-Schalter iC60L, 2P, 63A, B Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  3P","Acti9",null,"Schneider",null,null,null,null,0,"LS-Schalter  3P"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 2A, B Charakteristik","A9F93302","100kA","Schneider",2,1.9,{"$f":"3*G1232","v":5.6999999999999993},null,1.9,"LS-Schalter iC60L, 3P, 2A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 6A, B Charakteristik","A9F93306","25kA","Schneider",6,1.3,{"$f":"3*G1233","v":3.9000000000000004},null,1.3,"LS-Schalter iC60L, 3P, 6A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 10A, B Charakteristik","A9F93310","25kA","Schneider",10,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60L, 3P, 10A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 13A, B Charakteristik","A9F93313","25kA","Schneider",13,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60L, 3P, 13A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 16A, B Charakteristik","A9F93316","25kA","Schneider",16,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60L, 3P, 16A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 20A, B Charakteristik","A9F93320","25kA","Schneider",20,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60L, 3P, 20A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 25A, B Charakteristik","A9F93325","25kA","Schneider",25,3,9,null,3,"LS-Schalter iC60L, 3P, 25A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 32A, B Charakteristik","A9F93332","20kA","Schneider",32,2.8,8.3999999999999986,null,2.8,"LS-Schalter iC60L, 3P, 32A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 40A, B Charakteristik","A9F93340","20kA","Schneider",40,3.6,10.8,null,3.6,"LS-Schalter iC60L, 3P, 40A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 50A, B Charakteristik","A9F93350","15kA","Schneider",50,4,12,null,4,"LS-Schalter iC60L, 3P, 50A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 63A, B Charakteristik","A9F93363","15kA","Schneider",63,5.6,16.799999999999997,null,5.6,"LS-Schalter iC60L, 3P, 63A, B Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  3P+N","Acti9",null,"Schneider",null,null,null,null,0,"LS-Schalter  3P+N"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P+N, 6A, B Charakteristik","A9F93706","25kA","Schneider",6,1.3,{"$f":"3*G1245","v":3.9000000000000004},null,1.3,"LS-Schalter iC60L, 3P+N, 6A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P+N, 10A, B Charakteristik","A9F93710","25kA","Schneider",10,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60L, 3P+N, 10A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P+N, 13A, B Charakteristik","A9F93713","25kA","Schneider",13,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60L, 3P+N, 13A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P+N, 16A, B Charakteristik","A9F93716","25kA","Schneider",16,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60L, 3P+N, 16A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P+N, 20A, B Charakteristik","A9F93720","25kA","Schneider",20,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60L, 3P+N, 20A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P+N, 25A, B Charakteristik","A9F93725","25kA","Schneider",25,3,9,null,3,"LS-Schalter iC60L, 3P+N, 25A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P+N, 32A, B Charakteristik","A9F93732","20kA","Schneider",32,2.8,8.3999999999999986,null,2.8,"LS-Schalter iC60L, 3P+N, 32A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P+N, 40A, B Charakteristik","A9F93740","20kA","Schneider",40,3.6,10.8,null,3.6,"LS-Schalter iC60L, 3P+N, 40A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P+N, 50A, B Charakteristik","A9F93750","15kA","Schneider",50,4,12,null,4,"LS-Schalter iC60L, 3P+N, 50A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P+N, 63A, B Charakteristik","A9F93763","15kA","Schneider",63,5.6,16.799999999999997,null,5.6,"LS-Schalter iC60L, 3P+N, 63A, B Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  4P","Acti9",null,"Schneider",null,null,null,null,0,"LS-Schalter  4P"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 6A, B Charakteristik","A9F93406","25kA","Schneider",6,1.3,{"$f":"3*G1257","v":3.9000000000000004},null,1.3,"LS-Schalter iC60L, 4P, 6A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 10A, B Charakteristik","A9F93410","25kA","Schneider",10,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60L, 4P, 10A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 13A, B Charakteristik","A9F93413","25kA","Schneider",13,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60L, 4P, 13A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 16A, B Charakteristik","A9F93416","25kA","Schneider",16,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60L, 4P, 16A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 20A, B Charakteristik","A9F93420","25kA","Schneider",20,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60L, 4P, 20A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 25A, B Charakteristik","A9F93425","25kA","Schneider",25,3,9,null,3,"LS-Schalter iC60L, 4P, 25A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 32A, B Charakteristik","A9F93432","20kA","Schneider",32,2.8,8.3999999999999986,null,2.8,"LS-Schalter iC60L, 4P, 32A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 40A, B Charakteristik","A9F93440","20kA","Schneider",40,3.6,10.8,null,3.6,"LS-Schalter iC60L, 4P, 40A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 50A, B Charakteristik","A9F93450","15kA","Schneider",50,4,12,null,4,"LS-Schalter iC60L, 4P, 50A, B Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 63A, B Charakteristik","A9F93463","15kA","Schneider",63,5.6,16.799999999999997,null,5.6,"LS-Schalter iC60L, 4P, 63A, B Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  1P","Acti9",null,"Schneider",null,null,null,null,0,"LS-Schalter  1P"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 1A, C Charakteristik","A9F94101","100kA","Schneider",1,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60L, 1P, 1A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 2A, C Charakteristik","A9F94102","100kA","Schneider",2,1.9,1.9,null,1.9,"LS-Schalter iC60L, 1P, 2A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 3A, C Charakteristik","A9F94103","100kA","Schneider",3,2.2000000000000002,2.2000000000000002,null,2.2000000000000002,"LS-Schalter iC60L, 1P, 3A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 4A, C Charakteristik","A9F94104","100kA","Schneider",4,2.4,2.4,null,2.4,"LS-Schalter iC60L, 1P, 4A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 6A, C Charakteristik","A9F94106","25kA","Schneider",6,1.3,1.3,null,1.3,"LS-Schalter iC60L, 1P, 6A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 10A, C Charakteristik","A9F94110","25kA","Schneider",10,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60L, 1P, 10A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 13A, C Charakteristik","A9F94113","25kA","Schneider",13,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60L, 1P, 13A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 16A, C Charakteristik","A9F94116","25kA","Schneider",16,2.4,2.4,null,2.4,"LS-Schalter iC60L, 1P, 16A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 20A, C Charakteristik","A9F94120","25kA","Schneider",20,2.4,2.4,null,2.4,"LS-Schalter iC60L, 1P, 20A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 25A, C Charakteristik","A9F94125","25kA","Schneider",25,3,3,null,3,"LS-Schalter iC60L, 1P, 25A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 32A, C Charakteristik","A9F94132","20kA","Schneider",32,2.8,2.8,null,2.8,"LS-Schalter iC60L, 1P, 32A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 40A, C Charakteristik","A9F94140","20kA","Schneider",40,3.6,3.6,null,{"$f":"G1280+I1280","v":3.6},"LS-Schalter iC60L, 1P, 40A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 50A, C Charakteristik","A9F94150","15kA","Schneider",50,4,4,null,4,"LS-Schalter iC60L, 1P, 50A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 63A, C Charakteristik","A9F94163","15kA","Schneider",63,5.6,5.6,null,5.6,"LS-Schalter iC60L, 1P, 63A, C Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  1P+N","Acti9",null,"Schneider",null,null,null,null,0,"LS-Schalter  1P+N"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P+N, 1A, C Charakteristik","A9F94601","100kA","Schneider",1,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60L, 1P+N, 1A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P+N, 2A, C Charakteristik","A9F94602","100kA","Schneider",2,1.9,1.9,null,1.9,"LS-Schalter iC60L, 1P+N, 2A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P+N, 3A, C Charakteristik","A9F94603","100kA","Schneider",3,2.2000000000000002,2.2000000000000002,null,2.2000000000000002,"LS-Schalter iC60L, 1P+N, 3A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P+N, 4A, C Charakteristik","A9F94604","100kA","Schneider",4,2.4,2.4,null,2.4,"LS-Schalter iC60L, 1P+N, 4A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P+N, 6A, C Charakteristik","A9F94606","25kA","Schneider",6,1.3,1.3,null,1.3,"LS-Schalter iC60L, 1P+N, 6A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P+N, 10A, C Charakteristik","A9F94610","25kA","Schneider",10,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60L, 1P+N, 10A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P+N, 13A, C Charakteristik","A9F94613","25kA","Schneider",13,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60L, 1P+N, 13A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P+N, 16A, C Charakteristik","A9F94616","25kA","Schneider",16,2.4,2.4,null,2.4,"LS-Schalter iC60L, 1P+N, 16A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P+N, 20A, C Charakteristik","A9F94620","25kA","Schneider",20,2.4,2.4,null,2.4,"LS-Schalter iC60L, 1P+N, 20A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P+N, 25A, C Charakteristik","A9F94625","25kA","Schneider",25,3,3,null,3,"LS-Schalter iC60L, 1P+N, 25A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P+N, 32A, C Charakteristik","A9F94632","20kA","Schneider",32,2.8,2.8,null,2.8,"LS-Schalter iC60L, 1P+N, 32A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P+N, 40A, C Charakteristik","A9F94640","20kA","Schneider",40,3.6,3.6,null,3.6,"LS-Schalter iC60L, 1P+N, 40A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P+N, 50A, C Charakteristik","A9F94650","15kA","Schneider",50,4,4,null,4,"LS-Schalter iC60L, 1P+N, 50A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P+N, 63A, C Charakteristik","A9F94663","15kA","Schneider",63,5.6,5.6,null,5.6,"LS-Schalter iC60L, 1P+N, 63A, C Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  2P","Acti9",null,"Schneider",null,null,null,null,0,"LS-Schalter  2P"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 1A, C Charakteristik","A9F94201","100kA","Schneider",1,2.2999999999999998,{"$f":"2*G1301","v":4.5999999999999996},null,2.2999999999999998,"LS-Schalter iC60L, 2P, 1A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 2A, C Charakteristik","A9F94202","100kA","Schneider",2,1.9,{"$f":"2*G1302","v":3.8},null,1.9,"LS-Schalter iC60L, 2P, 2A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 3A, C Charakteristik","A9F94203","100kA","Schneider",3,2.2000000000000002,4.4000000000000004,null,2.2000000000000002,"LS-Schalter iC60L, 2P, 3A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 4A, C Charakteristik","A9F94204","100kA","Schneider",4,2.4,4.8,null,2.4,"LS-Schalter iC60L, 2P, 4A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 6A, C Charakteristik","A9F94206","25kA","Schneider",6,1.3,2.6,null,1.3,"LS-Schalter iC60L, 2P, 6A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 10A, C Charakteristik","A9F94210","25kA","Schneider",10,2.2999999999999998,4.5999999999999996,null,2.2999999999999998,"LS-Schalter iC60L, 2P, 10A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 13A, C Charakteristik","A9F94213","25kA","Schneider",13,2.2999999999999998,4.5999999999999996,null,2.2999999999999998,"LS-Schalter iC60L, 2P, 13A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 16A, C Charakteristik","A9F94216","25kA","Schneider",16,2.4,4.8,null,2.4,"LS-Schalter iC60L, 2P, 16A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 20A, C Charakteristik","A9F94220","25kA","Schneider",20,2.4,4.8,null,2.4,"LS-Schalter iC60L, 2P, 20A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 25A, C Charakteristik","A9F94225","25kA","Schneider",25,3,6,null,3,"LS-Schalter iC60L, 2P, 25A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 32A, C Charakteristik","A9F94232","20kA","Schneider",32,2.8,5.6,null,2.8,"LS-Schalter iC60L, 2P, 32A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 40A, C Charakteristik","A9F94240","20kA","Schneider",40,3.6,7.2,null,3.6,"LS-Schalter iC60L, 2P, 40A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 50A, C Charakteristik","A9F94250","15kA","Schneider",50,4,8,null,4,"LS-Schalter iC60L, 2P, 50A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 63A, C Charakteristik","A9F94263","15kA","Schneider",63,5.6,11.2,null,5.6,"LS-Schalter iC60L, 2P, 63A, C Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  3P","Acti9",null,"Schneider",null,null,null,null,0,"LS-Schalter  3P"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 1A, C Charakteristik","A9F94301","100kA","Schneider",1,2.2999999999999998,{"$f":"3*G1317","v":6.8999999999999995},null,2.2999999999999998,"LS-Schalter iC60L, 3P, 1A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 2A, C Charakteristik","A9F94302","100kA","Schneider",2,1.9,{"$f":"3*G1318","v":5.6999999999999993},null,1.9,"LS-Schalter iC60L, 3P, 2A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 3A, C Charakteristik","A9F94303","100kA","Schneider",3,2.2000000000000002,6.6000000000000005,null,2.2000000000000002,"LS-Schalter iC60L, 3P, 3A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 4A, C Charakteristik","A9F94304","100kA","Schneider",4,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60L, 3P, 4A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 6A, C Charakteristik","A9F94306","25kA","Schneider",6,1.3,3.9000000000000004,null,1.3,"LS-Schalter iC60L, 3P, 6A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 10A, C Charakteristik","A9F94310","25kA","Schneider",10,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60L, 3P, 10A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 13A, C Charakteristik","A9F94313","25kA","Schneider",13,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60L, 3P, 13A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 16A, C Charakteristik","A9F94316","25kA","Schneider",16,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60L, 3P, 16A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 20A, C Charakteristik","A9F94320","25kA","Schneider",20,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60L, 3P, 20A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 25A, C Charakteristik","A9F94325","25kA","Schneider",25,3,9,null,3,"LS-Schalter iC60L, 3P, 25A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 32A, C Charakteristik","A9F94332","20kA","Schneider",32,2.8,8.3999999999999986,null,2.8,"LS-Schalter iC60L, 3P, 32A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 40A, C Charakteristik","A9F94340","20kA","Schneider",40,3.6,10.8,null,3.6,"LS-Schalter iC60L, 3P, 40A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 50A, C Charakteristik","A9F94350","15kA","Schneider",50,4,12,null,4,"LS-Schalter iC60L, 3P, 50A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 63A, C Charakteristik","A9F94363","15kA","Schneider",63,5.6,16.799999999999997,null,5.6,"LS-Schalter iC60L, 3P, 63A, C Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  3P+N","Acti9",null,"Schneider",null,null,null,null,0,"LS-Schalter  3P+N"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P+N, 1A, C Charakteristik","A9F94701","100kA","Schneider",1,2.2999999999999998,{"$f":"3*G1333","v":6.8999999999999995},null,2.2999999999999998,"LS-Schalter iC60L, 3P+N, 1A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P+N, 2A, C Charakteristik","A9F94702","100kA","Schneider",2,1.9,{"$f":"3*G1334","v":5.6999999999999993},null,1.9,"LS-Schalter iC60L, 3P+N, 2A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P+N, 3A, C Charakteristik","A9F94703","100kA","Schneider",3,2.2000000000000002,6.6000000000000005,null,2.2000000000000002,"LS-Schalter iC60L, 3P+N, 3A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P+N, 4A, C Charakteristik","A9F94704","100kA","Schneider",4,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60L, 3P+N, 4A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P+N, 6A, C Charakteristik","A9F94706","25kA","Schneider",6,1.3,3.9000000000000004,null,1.3,"LS-Schalter iC60L, 3P+N, 6A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P+N, 10A, C Charakteristik","A9F94710","25kA","Schneider",10,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60L, 3P+N, 10A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P+N, 13A, C Charakteristik","A9F94713","25kA","Schneider",13,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60L, 3P+N, 13A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P+N, 16A, C Charakteristik","A9F94716","25kA","Schneider",16,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60L, 3P+N, 16A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P+N, 20A, C Charakteristik","A9F94720","25kA","Schneider",20,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60L, 3P+N, 20A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P+N, 25A, C Charakteristik","A9F94725","25kA","Schneider",25,3,9,null,3,"LS-Schalter iC60L, 3P+N, 25A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P+N, 32A, C Charakteristik","A9F94732","20kA","Schneider",32,2.8,8.3999999999999986,null,2.8,"LS-Schalter iC60L, 3P+N, 32A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P+N, 40A, C Charakteristik","A9F94740","20kA","Schneider",40,3.6,10.8,null,{"$f":"G1344+I1344","v":3.6},"LS-Schalter iC60L, 3P+N, 40A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P+N, 50A, C Charakteristik","A9F94750","15kA","Schneider",50,4,12,null,4,"LS-Schalter iC60L, 3P+N, 50A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P+N, 63A, C Charakteristik","A9F94763","15kA","Schneider",63,5.6,16.799999999999997,null,5.6,"LS-Schalter iC60L, 3P+N, 63A, C Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  4P","Acti9",null,"Schneider",null,null,null,null,0,"LS-Schalter  4P"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 1A, C Charakteristik","A9F94401","100kA","Schneider",1,2.2999999999999998,{"$f":"3*G1349","v":6.8999999999999995},null,2.2999999999999998,"LS-Schalter iC60L, 4P, 1A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 2A, C Charakteristik","A9F94402","100kA","Schneider",2,1.9,{"$f":"3*G1350","v":5.6999999999999993},null,1.9,"LS-Schalter iC60L, 4P, 2A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 3A, C Charakteristik","A9F94403","100kA","Schneider",3,2.2000000000000002,6.6000000000000005,null,2.2000000000000002,"LS-Schalter iC60L, 4P, 3A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 4A, C Charakteristik","A9F94404","100kA","Schneider",4,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60L, 4P, 4A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 6A, C Charakteristik","A9F94406","25kA","Schneider",6,1.3,3.9000000000000004,null,1.3,"LS-Schalter iC60L, 4P, 6A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 10A, C Charakteristik","A9F94410","25kA","Schneider",10,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60L, 4P, 10A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 13A, C Charakteristik","A9F94413","25kA","Schneider",13,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60L, 4P, 13A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 16A, C Charakteristik","A9F94416","25kA","Schneider",16,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60L, 4P, 16A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 20A, C Charakteristik","A9F94420","25kA","Schneider",20,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60L, 4P, 20A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 25A, C Charakteristik","A9F94425","25kA","Schneider",25,3,9,null,3,"LS-Schalter iC60L, 4P, 25A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 32A, C Charakteristik","A9F94432","20kA","Schneider",32,2.8,8.3999999999999986,null,2.8,"LS-Schalter iC60L, 4P, 32A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 40A, C Charakteristik","A9F94440","20kA","Schneider",40,3.6,10.8,null,3.6,"LS-Schalter iC60L, 4P, 40A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 50A, C Charakteristik","A9F94450","15kA","Schneider",50,4,12,null,4,"LS-Schalter iC60L, 4P, 50A, C Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 63A, C Charakteristik","A9F94463","15kA","Schneider",63,5.6,16.799999999999997,null,5.6,"LS-Schalter iC60L, 4P, 63A, C Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  2P","Acti9",null,"Schneider",null,null,null,null,0,"LS-Schalter  2P"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 4A, MA Charakteristik","A9F90204","20kA","Schneider",4,2.4,{"$f":"2*G1365","v":4.8},null,2.4,"LS-Schalter iC60L, 2P, 4A, MA Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 10A, MA Charakteristik","A9F90210","15kA","Schneider",10,2.2999999999999998,4.5999999999999996,null,2.2999999999999998,"LS-Schalter iC60L, 2P, 10A, MA Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 20A, MA Charakteristik","A9F90220","15kA","Schneider",20,2.4,4.8,null,2.4,"LS-Schalter iC60L, 2P, 20A, MA Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 25A, MA Charakteristik","A9F90225","15kA","Schneider",25,3,6,null,3,"LS-Schalter iC60L, 2P, 25A, MA Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 40A, MA Charakteristik","A9F90240","15kA","Schneider",40,3.6,7.2,null,3.6,"LS-Schalter iC60L, 2P, 40A, MA Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  3P","Acti9",null,"Schneider",null,null,null,null,0,"LS-Schalter  3P"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 4A, MA Charakteristik","A9F90304","20kA","Schneider",4,2.4,{"$f":"3*G1372","v":7.1999999999999993},null,2.4,"LS-Schalter iC60L, 3P, 4A, MA Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 10A, MA Charakteristik","A9F90310","15kA","Schneider",10,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60L, 3P, 10A, MA Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 20A, MA Charakteristik","A9F90320","15kA","Schneider",20,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60L, 3P, 20A, MA Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 25A, MA Charakteristik","A9F90325","15kA","Schneider",25,3,9,null,3,"LS-Schalter iC60L, 3P, 25A, MA Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 40A, MA Charakteristik","A9F90340","15kA","Schneider",40,3.6,10.8,null,3.6,"LS-Schalter iC60L, 3P, 40A, MA Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  1P","Acti9",null,"Schneider",null,null,null,null,0,"LS-Schalter  1P"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 1A, Z Charakteristik","A9F92101","100kA","Schneider",1,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60L, 1P, 1A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 2A, Z Charakteristik","A9F92102","100kA","Schneider",2,1.9,1.9,null,1.9,"LS-Schalter iC60L, 1P, 2A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 3A, Z Charakteristik","A9F92103","100kA","Schneider",3,2.2000000000000002,2.2000000000000002,null,2.2000000000000002,"LS-Schalter iC60L, 1P, 3A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 4A, Z Charakteristik","A9F92104","100kA","Schneider",4,2.4,2.4,null,2.4,"LS-Schalter iC60L, 1P, 4A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 6A, Z Charakteristik","A9F92106","25kA","Schneider",6,1.3,1.3,null,1.3,"LS-Schalter iC60L, 1P, 6A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 10A, Z Charakteristik","A9F92110","25kA","Schneider",10,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60L, 1P, 10A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 13A, Z Charakteristik","A9F92113","25kA","Schneider",13,2.2999999999999998,2.2999999999999998,null,2.2999999999999998,"LS-Schalter iC60L, 1P, 13A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 16A, Z Charakteristik","A9F92116","25kA","Schneider",16,2.4,2.4,null,2.4,"LS-Schalter iC60L, 1P, 16A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 20A, Z Charakteristik","A9F92120","25kA","Schneider",20,2.4,2.4,null,2.4,"LS-Schalter iC60L, 1P, 20A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 25A, Z Charakteristik","A9F92125","25kA","Schneider",25,3,3,null,3,"LS-Schalter iC60L, 1P, 25A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 32A, Z Charakteristik","A9F92132","20kA","Schneider",32,2.8,2.8,null,2.8,"LS-Schalter iC60L, 1P, 32A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 40A, Z Charakteristik","A9F92140","20kA","Schneider",40,3.6,3.6,null,3.6,"LS-Schalter iC60L, 1P, 40A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 50A, Z Charakteristik","A9F92150","15kA","Schneider",50,4,4,null,4,"LS-Schalter iC60L, 1P, 50A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 1P, 63A, Z Charakteristik","A9F92163","15kA","Schneider",63,5.6,5.6,null,5.6,"LS-Schalter iC60L, 1P, 63A, Z Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  2P","Acti9",null,"Schneider",null,null,null,null,0,"LS-Schalter  2P"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 1A, Z Charakteristik","A9F92201","100kA","Schneider",1,2.2999999999999998,{"$f":"2*G1395","v":4.5999999999999996},null,2.2999999999999998,"LS-Schalter iC60L, 2P, 1A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 2A, Z Charakteristik","A9F92202","100kA","Schneider",2,1.9,{"$f":"2*G1396","v":3.8},null,1.9,"LS-Schalter iC60L, 2P, 2A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 3A, Z Charakteristik","A9F92203","100kA","Schneider",3,2.2000000000000002,4.4000000000000004,null,2.2000000000000002,"LS-Schalter iC60L, 2P, 3A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 4A, Z Charakteristik","A9F92204","100kA","Schneider",4,2.4,4.8,null,2.4,"LS-Schalter iC60L, 2P, 4A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 6A, Z Charakteristik","A9F92206","25kA","Schneider",6,1.3,2.6,null,1.3,"LS-Schalter iC60L, 2P, 6A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 10A, Z Charakteristik","A9F92210","25kA","Schneider",10,2.2999999999999998,4.5999999999999996,null,2.2999999999999998,"LS-Schalter iC60L, 2P, 10A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 13A, Z Charakteristik","A9F92213","25kA","Schneider",13,2.2999999999999998,4.5999999999999996,null,2.2999999999999998,"LS-Schalter iC60L, 2P, 13A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 16A, Z Charakteristik","A9F92216","25kA","Schneider",16,2.4,4.8,null,2.4,"LS-Schalter iC60L, 2P, 16A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 20A, Z Charakteristik","A9F92220","25kA","Schneider",20,2.4,4.8,null,2.4,"LS-Schalter iC60L, 2P, 20A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 25A, Z Charakteristik","A9F92225","25kA","Schneider",25,3,6,null,3,"LS-Schalter iC60L, 2P, 25A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 32A, Z Charakteristik","A9F92232","20kA","Schneider",32,2.8,5.6,null,2.8,"LS-Schalter iC60L, 2P, 32A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 40A, Z Charakteristik","A9F92240","20kA","Schneider",40,3.6,7.2,null,3.6,"LS-Schalter iC60L, 2P, 40A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 50A, Z Charakteristik","A9F92250","15kA","Schneider",50,4,8,null,4,"LS-Schalter iC60L, 2P, 50A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 2P, 63A, Z Charakteristik","A9F92263","15kA","Schneider",63,5.6,11.2,null,{"$f":"G1408+I1408","v":5.6},"LS-Schalter iC60L, 2P, 63A, Z Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  3P","Acti9",null,"Schneider",null,null,null,null,0,"LS-Schalter  3P"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 1A, Z Charakteristik","A9F92301","100kA","Schneider",1,2.2999999999999998,{"$f":"3*G1411","v":6.8999999999999995},null,2.2999999999999998,"LS-Schalter iC60L, 3P, 1A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 2A, Z Charakteristik","A9F92302","100kA","Schneider",2,1.9,{"$f":"3*G1412","v":5.6999999999999993},null,1.9,"LS-Schalter iC60L, 3P, 2A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 3A, Z Charakteristik","A9F92303","100kA","Schneider",3,2.2000000000000002,6.6000000000000005,null,2.2000000000000002,"LS-Schalter iC60L, 3P, 3A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 4A, Z Charakteristik","A9F92304","100kA","Schneider",4,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60L, 3P, 4A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 6A, Z Charakteristik","A9F92306","25kA","Schneider",6,1.3,3.9000000000000004,null,1.3,"LS-Schalter iC60L, 3P, 6A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 10A, Z Charakteristik","A9F92310","25kA","Schneider",10,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60L, 3P, 10A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 13A, Z Charakteristik","A9F92313","25kA","Schneider",13,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60L, 3P, 13A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 16A, Z Charakteristik","A9F92316","25kA","Schneider",16,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60L, 3P, 16A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 20A, Z Charakteristik","A9F92320","25kA","Schneider",20,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60L, 3P, 20A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 25A, Z Charakteristik","A9F92325","25kA","Schneider",25,3,9,null,3,"LS-Schalter iC60L, 3P, 25A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 32A, Z Charakteristik","A9F92332","20kA","Schneider",32,2.8,8.3999999999999986,null,2.8,"LS-Schalter iC60L, 3P, 32A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 40A, Z Charakteristik","A9F92340","20kA","Schneider",40,3.6,10.8,null,3.6,"LS-Schalter iC60L, 3P, 40A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 50A, Z Charakteristik","A9F92350","15kA","Schneider",50,4,12,null,4,"LS-Schalter iC60L, 3P, 50A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 3P, 63A, Z Charakteristik","A9F92363","15kA","Schneider",63,5.6,16.799999999999997,null,5.6,"LS-Schalter iC60L, 3P, 63A, Z Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  4P","Acti9",null,"Schneider",null,null,null,null,0,"LS-Schalter  4P"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 1A, Z Charakteristik","A9F92401","100kA","Schneider",1,2.2999999999999998,{"$f":"3*G1427","v":6.8999999999999995},null,2.2999999999999998,"LS-Schalter iC60L, 4P, 1A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 2A, Z Charakteristik","A9F92402","100kA","Schneider",2,1.9,{"$f":"3*G1428","v":5.6999999999999993},null,1.9,"LS-Schalter iC60L, 4P, 2A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 3A, Z Charakteristik","A9F92403","100kA","Schneider",3,2.2000000000000002,6.6000000000000005,null,2.2000000000000002,"LS-Schalter iC60L, 4P, 3A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 4A, Z Charakteristik","A9F92404","100kA","Schneider",4,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60L, 4P, 4A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 6A, Z Charakteristik","A9F92406","25kA","Schneider",6,1.3,3.9000000000000004,null,1.3,"LS-Schalter iC60L, 4P, 6A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 10A, Z Charakteristik","A9F92410","25kA","Schneider",10,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60L, 4P, 10A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 13A, Z Charakteristik","A9F92413","25kA","Schneider",13,2.2999999999999998,6.8999999999999995,null,2.2999999999999998,"LS-Schalter iC60L, 4P, 13A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 16A, Z Charakteristik","A9F92416","25kA","Schneider",16,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60L, 4P, 16A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 20A, Z Charakteristik","A9F92420","25kA","Schneider",20,2.4,7.1999999999999993,null,2.4,"LS-Schalter iC60L, 4P, 20A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 25A, Z Charakteristik","A9F92425","25kA","Schneider",25,3,9,null,3,"LS-Schalter iC60L, 4P, 25A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 32A, Z Charakteristik","A9F92432","20kA","Schneider",32,2.8,8.3999999999999986,null,2.8,"LS-Schalter iC60L, 4P, 32A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 40A, Z Charakteristik","A9F92440","20kA","Schneider",40,3.6,10.8,null,3.6,"LS-Schalter iC60L, 4P, 40A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 50A, Z Charakteristik","A9F92450","15kA","Schneider",50,4,12,null,4,"LS-Schalter iC60L, 4P, 50A, Z Charakteristik"]
["Leistungsschalter REG","LS-Schalter iC60L, 4P, 63A, Z Charakteristik","A9F92463","15kA","Schneider",63,5.6,16.799999999999997,null,5.6,"LS-Schalter iC60L, 4P, 63A, Z Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  1P",null,null,null,null,null,null,null,0,"LS-Schalter  1P"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 1p, 80A, B Charakteristik","A9N18341","10kA","Schneider",80,4.5,4.5,null,4.5,"Leitungsschutzschalter C120N, 1p, 80A, B Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 1p, 100A, B Charakteristik","A9N18342","10kA","Schneider",100,6,6,null,6,"Leitungsschutzschalter C120N, 1p, 100A, B Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 1p, 125A, B Charakteristik","A9N18343","10kA","Schneider",125,8,8,null,8,"Leitungsschutzschalter C120N, 1p, 125A, B Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  2P",null,null,null,null,null,null,null,0,"LS-Schalter  2P"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 2p, 80A, B Charakteristik","A9N18345","10kA","Schneider",80,4.5,{"$f":"G1448*2","v":9},null,4.5,"Leitungsschutzschalter C120N, 2p, 80A, B Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 2p, 100A, B Charakteristik","A9N18346","10kA","Schneider",100,6,{"$f":"G1449*2","v":12},null,6,"Leitungsschutzschalter C120N, 2p, 100A, B Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 2p, 125A, B Charakteristik","A9N18347","10kA","Schneider",125,8,16,null,8,"Leitungsschutzschalter C120N, 2p, 125A, B Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  3P",null,null,null,null,null,null,null,0,"LS-Schalter  3P"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 3p, 80A, B Charakteristik","A9N18349","10kA","Schneider",80,4.5,{"$f":"G1453*3","v":13.5},null,4.5,"Leitungsschutzschalter C120N, 3p, 80A, B Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 3p, 100A, B Charakteristik","A9N18350","10kA","Schneider",100,6,18,null,6,"Leitungsschutzschalter C120N, 3p, 100A, B Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 3p, 125A, B Charakteristik","A9N18351","10kA","Schneider",125,8,24,null,8,"Leitungsschutzschalter C120N, 3p, 125A, B Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  4P",null,null,null,null,null,null,null,0,"LS-Schalter  4P"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 4p, 80A, B Charakteristik","A9N18353","10kA","Schneider",80,4.5,13.5,null,4.5,"Leitungsschutzschalter C120N, 4p, 80A, B Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 4p, 100A, B Charakteristik","A9N18354","10kA","Schneider",100,6,18,null,6,"Leitungsschutzschalter C120N, 4p, 100A, B Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 4p, 125A, B Charakteristik","A9N18355","10kA","Schneider",125,8,24,null,8,"Leitungsschutzschalter C120N, 4p, 125A, B Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  1P",null,null,null,null,null,null,null,0,"LS-Schalter  1P"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 1p, 80A, C Charakteristik","A9N18357","10kA","Schneider",80,4.5,4.5,null,4.5,"Leitungsschutzschalter C120N, 1p, 80A, C Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 1p, 100A, C Charakteristik","A9N18358","10kA","Schneider",100,6,6,null,6,"Leitungsschutzschalter C120N, 1p, 100A, C Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 1p, 125A, C Charakteristik","A9N18359","10kA","Schneider",125,8,8,null,8,"Leitungsschutzschalter C120N, 1p, 125A, C Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  2P",null,null,null,null,null,null,null,0,"LS-Schalter  2P"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 2p, 80A, C Charakteristik","A9N18361","10kA","Schneider",80,4.5,{"$f":"G1468*2","v":9},null,4.5,"Leitungsschutzschalter C120N, 2p, 80A, C Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 2p, 100A, C Charakteristik","A9N18362","10kA","Schneider",100,6,{"$f":"G1469*2","v":12},null,6,"Leitungsschutzschalter C120N, 2p, 100A, C Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 2p, 125A, C Charakteristik","A9N18363","10kA","Schneider",125,8,16,null,8,"Leitungsschutzschalter C120N, 2p, 125A, C Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  3P",null,null,null,null,null,null,null,{"$f":"G1472+I1472","v":0},"LS-Schalter  3P"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 3p, 80A, C Charakteristik","A9N18365","10kA","Schneider",80,4.5,13.5,null,4.5,"Leitungsschutzschalter C120N, 3p, 80A, C Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 3p, 100A, C Charakteristik","A9N18367","10kA","Schneider",100,6,18,null,6,"Leitungsschutzschalter C120N, 3p, 100A, C Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 3p, 125A, C Charakteristik","A9N18369","10kA","Schneider",125,8,24,null,8,"Leitungsschutzschalter C120N, 3p, 125A, C Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  4P",null,null,null,null,null,null,null,0,"LS-Schalter  4P"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 4p, 80A, C Charakteristik","A9N18372","10kA","Schneider",80,4.5,13.5,null,4.5,"Leitungsschutzschalter C120N, 4p, 80A, C Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 4p, 100A, C Charakteristik","A9N18374","10kA","Schneider",100,6,18,null,6,"Leitungsschutzschalter C120N, 4p, 100A, C Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 4p, 125A, C Charakteristik","A9N18376","10kA","Schneider",125,8,24,null,8,"Leitungsschutzschalter C120N, 4p, 125A, C Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  1P",null,null,null,null,null,null,null,0,"LS-Schalter  1P"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 1p, 80A, D Charakteristik","A9N18379","10kA","Schneider",80,4.5,4.5,null,4.5,"Leitungsschutzschalter C120N, 1p, 80A, D Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 1p, 100A, D Charakteristik","A9N18380","10kA","Schneider",100,6,6,null,6,"Leitungsschutzschalter C120N, 1p, 100A, D Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 1p, 125A, D Charakteristik","A9N18381","10kA","Schneider",125,8,8,null,8,"Leitungsschutzschalter C120N, 1p, 125A, D Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  2P",null,null,null,null,null,null,null,0,"LS-Schalter  2P"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 2p, 80A, D Charakteristik","A9N18383","10kA","Schneider",80,4.5,{"$f":"G1488*2","v":9},null,4.5,"Leitungsschutzschalter C120N, 2p, 80A, D Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 2p, 100A, D Charakteristik","A9N18384","10kA","Schneider",100,6,{"$f":"G1489*2","v":12},null,6,"Leitungsschutzschalter C120N, 2p, 100A, D Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 2p, 125A, D Charakteristik","A9N18385","10kA","Schneider",125,8,16,null,8,"Leitungsschutzschalter C120N, 2p, 125A, D Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  3P",null,null,null,null,null,null,null,0,"LS-Schalter  3P"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 3p, 80A, D Charakteristik","A9N18387","10kA","Schneider",80,4.5,{"$f":"G1493*3","v":13.5},null,4.5,"Leitungsschutzschalter C120N, 3p, 80A, D Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 3p, 100A, D Charakteristik","A9N18388","10kA","Schneider",100,6,{"$f":"G1494*3","v":18},null,6,"Leitungsschutzschalter C120N, 3p, 100A, D Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 3p, 125A, D Charakteristik","A9N18389","10kA","Schneider",125,8,{"$f":"G1495*3","v":24},null,8,"Leitungsschutzschalter C120N, 3p, 125A, D Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  4P",null,null,null,null,null,null,null,0,"LS-Schalter  4P"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 4p, 80A, D Charakteristik","A9N18391","10kA","Schneider",80,4.5,{"$f":"G1498*3","v":13.5},null,4.5,"Leitungsschutzschalter C120N, 4p, 80A, D Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 4p, 100A, D Charakteristik","A9N18392","10kA","Schneider",100,6,{"$f":"G1499*3","v":18},null,6,"Leitungsschutzschalter C120N, 4p, 100A, D Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120N, 4p, 125A, D Charakteristik","A9N18393","10kA","Schneider",125,8,{"$f":"G1500*3","v":24},null,8,"Leitungsschutzschalter C120N, 4p, 125A, D Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  1P",null,null,null,null,null,null,null,0,"LS-Schalter  1P"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 1p, 63A, B Charakteristik","A9N18401","15kA","Schneider",63,4,4,null,4,"Leitungsschutzschalter C120H, 1p, 63A, B Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 1p, 80A, B Charakteristik","A9N18402","15kA","Schneider",80,4.5,4.5,null,4.5,"Leitungsschutzschalter C120H, 1p, 80A, B Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 1p, 100A, B Charakteristik","A9N18403","15kA","Schneider",100,6,6,null,6,"Leitungsschutzschalter C120H, 1p, 100A, B Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 1p, 125A, B Charakteristik","A9N18404","15kA","Schneider",125,8,8,null,8,"Leitungsschutzschalter C120H, 1p, 125A, B Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  2P",null,null,null,null,null,null,null,0,"LS-Schalter  2P"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 2p, 63A, B Charakteristik","A9N18412","15kA","Schneider",63,4,{"$f":"G1509*2","v":8},null,4,"Leitungsschutzschalter C120H, 2p, 63A, B Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 2p, 80A, B Charakteristik","A9N18413","15kA","Schneider",80,4.5,{"$f":"G1510*2","v":9},null,4.5,"Leitungsschutzschalter C120H, 2p, 80A, B Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 2p, 100A, B Charakteristik","A9N18414","15kA","Schneider",100,6,12,null,6,"Leitungsschutzschalter C120H, 2p, 100A, B Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 2p, 125A, B Charakteristik","A9N18415","15kA","Schneider",125,8,16,null,8,"Leitungsschutzschalter C120H, 2p, 125A, B Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  3P",null,null,null,null,null,null,null,0,"LS-Schalter  3P"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 3p, 63A, B Charakteristik","A9N18423","15kA","Schneider",63,4,{"$f":"G1515*3","v":12},null,4,"Leitungsschutzschalter C120H, 3p, 63A, B Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 3p, 80A, B Charakteristik","A9N18424","15kA","Schneider",80,4.5,13.5,null,4.5,"Leitungsschutzschalter C120H, 3p, 80A, B Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 3p, 100A, B Charakteristik","A9N18425","15kA","Schneider",100,6,18,null,6,"Leitungsschutzschalter C120H, 3p, 100A, B Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 3p, 125A, B Charakteristik","A9N18426","15kA","Schneider",125,8,24,null,8,"Leitungsschutzschalter C120H, 3p, 125A, B Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  4P",null,null,null,null,null,null,null,0,"LS-Schalter  4P"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 4p, 63A, B Charakteristik","A9N18434","15kA","Schneider",63,4,12,null,4,"Leitungsschutzschalter C120H, 4p, 63A, B Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 4p, 80A, B Charakteristik","A9N18435","15kA","Schneider",80,4.5,13.5,null,4.5,"Leitungsschutzschalter C120H, 4p, 80A, B Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 4p, 100A, B Charakteristik","A9N18436","15kA","Schneider",100,6,18,null,6,"Leitungsschutzschalter C120H, 4p, 100A, B Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 4p, 125A, B Charakteristik","A9N18437","15kA","Schneider",125,8,24,null,8,"Leitungsschutzschalter C120H, 4p, 125A, B Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  1P",null,null,null,null,null,null,null,0,"LS-Schalter  1P"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 1p, 63A, C Charakteristik","A9N18445","15kA","Schneider",63,4,4,null,4,"Leitungsschutzschalter C120H, 1p, 63A, C Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 1p, 80A, C Charakteristik","A9N18446","15kA","Schneider",80,4.5,4.5,null,4.5,"Leitungsschutzschalter C120H, 1p, 80A, C Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 1p, 100A, C Charakteristik","A9N18447","15kA","Schneider",100,6,6,null,6,"Leitungsschutzschalter C120H, 1p, 100A, C Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 1p, 125A, C Charakteristik","A9N18448","15kA","Schneider",125,8,8,null,8,"Leitungsschutzschalter C120H, 1p, 125A, C Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  2P",null,null,null,null,null,null,null,0,"LS-Schalter  2P"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 2p, 63A, C Charakteristik","A9N18456","15kA","Schneider",63,4,{"$f":"G1533*2","v":8},null,4,"Leitungsschutzschalter C120H, 2p, 63A, C Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 2p, 80A, C Charakteristik","A9N18457","15kA","Schneider",80,4.5,{"$f":"G1534*2","v":9},null,4.5,"Leitungsschutzschalter C120H, 2p, 80A, C Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 2p, 100A, C Charakteristik","A9N18458","15kA","Schneider",100,6,12,null,6,"Leitungsschutzschalter C120H, 2p, 100A, C Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 2p, 125A, C Charakteristik","A9N18459","15kA","Schneider",125,8,16,null,{"$f":"G1536+I1536","v":8},"Leitungsschutzschalter C120H, 2p, 125A, C Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  3P",null,null,null,null,null,null,null,0,"LS-Schalter  3P"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 3p, 63A, C Charakteristik","A9N18467","15kA","Schneider",63,4,12,null,4,"Leitungsschutzschalter C120H, 3p, 63A, C Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 3p, 80A, C Charakteristik","A9N18468","15kA","Schneider",80,4.5,13.5,null,4.5,"Leitungsschutzschalter C120H, 3p, 80A, C Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 3p, 100A, C Charakteristik","A9N18469","15kA","Schneider",100,6,18,null,6,"Leitungsschutzschalter C120H, 3p, 100A, C Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 3p, 125A, C Charakteristik","A9N18470","15kA","Schneider",125,8,24,null,8,"Leitungsschutzschalter C120H, 3p, 125A, C Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  4P",null,null,null,null,null,null,null,0,"LS-Schalter  4P"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 4p, 63A, C Charakteristik","A9N18478","15kA","Schneider",63,4,12,null,4,"Leitungsschutzschalter C120H, 4p, 63A, C Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 4p, 80A, C Charakteristik","A9N18479","15kA","Schneider",80,4.5,13.5,null,4.5,"Leitungsschutzschalter C120H, 4p, 80A, C Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 4p, 100A, C Charakteristik","A9N18480","15kA","Schneider",100,6,18,null,6,"Leitungsschutzschalter C120H, 4p, 100A, C Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 4p, 125A, C Charakteristik","A9N18481","15kA","Schneider",125,8,24,null,8,"Leitungsschutzschalter C120H, 4p, 125A, C Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  1P",null,null,null,null,null,null,null,0,"LS-Schalter  1P"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 1p, 63A, D Charakteristik","A9N18489","15kA","Schneider",63,4,4,null,4,"Leitungsschutzschalter C120H, 1p, 63A, D Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 1p, 80A, D Charakteristik","A9N18490","15kA","Schneider",80,4.5,4.5,null,4.5,"Leitungsschutzschalter C120H, 1p, 80A, D Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 1p, 100A, D Charakteristik","A9N18491","15kA","Schneider",100,6,6,null,6,"Leitungsschutzschalter C120H, 1p, 100A, D Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 1p, 125A, D Charakteristik","A9N18492","15kA","Schneider",125,8,8,null,8,"Leitungsschutzschalter C120H, 1p, 125A, D Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  2P",null,null,null,null,null,null,null,0,"LS-Schalter  2P"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 2p, 63A, D Charakteristik","A9N18500","15kA","Schneider",63,4,{"$f":"G1557*2","v":8},null,4,"Leitungsschutzschalter C120H, 2p, 63A, D Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 2p, 80A, D Charakteristik","A9N18501","15kA","Schneider",80,4.5,{"$f":"G1558*2","v":9},null,4.5,"Leitungsschutzschalter C120H, 2p, 80A, D Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 2p, 100A, D Charakteristik","A9N18502","15kA","Schneider",100,6,12,null,6,"Leitungsschutzschalter C120H, 2p, 100A, D Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 2p, 125A, D Charakteristik","A9N18503","15kA","Schneider",125,8,16,null,8,"Leitungsschutzschalter C120H, 2p, 125A, D Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  3P",null,null,null,null,null,null,null,0,"LS-Schalter  3P"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 3p, 63A, D Charakteristik","A9N18511","15kA","Schneider",63,4,12,null,4,"Leitungsschutzschalter C120H, 3p, 63A, D Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 3p, 80A, D Charakteristik","A9N18512","15kA","Schneider",80,4.5,13.5,null,4.5,"Leitungsschutzschalter C120H, 3p, 80A, D Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 3p, 100A, D Charakteristik","A9N18513","15kA","Schneider",100,6,18,null,6,"Leitungsschutzschalter C120H, 3p, 100A, D Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 3p, 125A, D Charakteristik","A9N18514","15kA","Schneider",125,8,24,null,8,"Leitungsschutzschalter C120H, 3p, 125A, D Charakteristik"]
["Leistungsschalter REG",null,null,null,null,null,null,null,null,0]
["Leistungsschalter REG","LS-Schalter  4P",null,null,null,null,null,null,null,0,"LS-Schalter  4P"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 4p, 63A, D Charakteristik","A9N18522","15kA","Schneider",63,4,{"$f":"G1569*3","v":12},null,4,"Leitungsschutzschalter C120H, 4p, 63A, D Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 4p, 80A, D Charakteristik","A9N18523","15kA","Schneider",80,4.5,13.5,null,4.5,"Leitungsschutzschalter C120H, 4p, 80A, D Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 4p, 100A, D Charakteristik","A9N18524","15kA","Schneider",100,6,18,null,6,"Leitungsschutzschalter C120H, 4p, 100A, D Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C120H, 4p, 125A, D Charakteristik","A9N18525","15kA","Schneider",125,8,24,null,8,"Leitungsschutzschalter C120H, 4p, 125A, D Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter Resi9 1P, 6A, B Charakteristik, 6kA","R9F23106",null,"Schneider",6,1.2,null,null,{"$f":"G1573+I1573","v":1.2},"Leitungsschutzschalter Resi9 1P, 6A, B Charakteristik, 6kA"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 1p, 16A, K Charakter istik","A9F95116",null,"Schneider",16,2.4,null,null,{"$f":"G1574+I1574","v":2.4},"Leitungsschutzschalter iC60L, 1p, 16A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 4p, 20A, K Charakter istik","A9F95420",null,"Schneider",20,2.4,null,null,2.4,"Leitungsschutzschalter iC60L, 4p, 20A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60N, 1p, 0,5A, C Charakte ristik","A9F04170",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60N, 1p, 0,5A, C Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60N, 2p, 0,5A, C Charakte ristik","A9F04270",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60N, 2p, 0,5A, C Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60N, 3p, 0,5A, C Charakte ristik","A9F04370",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60N, 3p, 0,5A, C Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60N, 4p, 0,5A, C Charakte ristik","A9F04470",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60N, 4p, 0,5A, C Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60N, 1p+N, 0,5A, C Charak teristik","A9F04670",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60N, 1p+N, 0,5A, C Charak teristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60N, 3p+N, 0,5A, C Charak teristik","A9F04770",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60N, 3p+N, 0,5A, C Charak teristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60N, 1p, 0,5A, D Charakte ristik","A9F05170",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60N, 1p, 0,5A, D Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60N, 2p, 0,5A, D Charakte ristik","A9F05270",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60N, 2p, 0,5A, D Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60N, 3p, 0,5A, 6kA D Charakteristik","A9F05370",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60N, 3p, 0,5A, 6kA D Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60N, 4p, 0,5A, D Charakte ristik","A9F05470",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60N, 4p, 0,5A, D Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60H, 1p, 0,5A, C 10kA","A9F07170",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60H, 1p, 0,5A, C 10kA"]
["Leistungsschalter REG","Leitungsschutzschalter iC60H, 2p, 0,5A, C Charakte ristik","A9F07270",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60H, 2p, 0,5A, C Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60H, 3p, 0,5A, C Charakte ristik","A9F07370",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60H, 3p, 0,5A, C Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60H, 4p, 0,5A, C Charakte ristik","A9F07470",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60H, 4p, 0,5A, C Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60H, 1p+N, 0,5A, C Charak teristik","A9F07670",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60H, 1p+N, 0,5A, C Charak teristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60H, 1p, 0,5A, D Charakte ristik","A9F08170",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60H, 1p, 0,5A, D Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60H, 2p, 0,5A, D Charakte ristik","A9F08270",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60H, 2p, 0,5A, D Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60H, 3p, 0,5A, D Charakte ristik","A9F08370",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60H, 3p, 0,5A, D Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60H, 4p, 0,5A, D Charakte ristik","A9F08470",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60H, 4p, 0,5A, D Charakte ristik"]
["Leistungsschalter REG","IC60N, Miniatur-Leistungsschalter, 2 P, 1A, D-Kurv e","A9F75201",null,"Schneider",1,2.2999999999999998,null,null,2.2999999999999998,"IC60N, Miniatur-Leistungsschalter, 2 P, 1A, D-Kurv e"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 16A, MA Charakte ristik","A9F90216",null,"Schneider",16,2.4,null,null,2.4,"Leitungsschutzschalter iC60L, 2p, 16A, MA Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 1,6A, MA Charakt eristik","A9F90272",null,"Schneider",1.6,2.6,null,null,2.6,"Leitungsschutzschalter iC60L, 2p, 1,6A, MA Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 2,5A, MA curve","A9F90273",null,"Schneider",2.5,2.2000000000000002,null,null,2.2000000000000002,"Leitungsschutzschalter iC60L, 2p, 2,5A, MA curve"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 6,3A, MA Charakt eristik","A9F90276",null,"Schneider",6.3,1.3,null,null,1.3,"Leitungsschutzschalter iC60L, 2p, 6,3A, MA Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 12,5A, MA Charak teristik","A9F90282",null,"Schneider",12.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 2p, 12,5A, MA Charak teristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 16A, MA Charakte ristik","A9F90316",null,"Schneider",16,2.4,null,null,2.4,"Leitungsschutzschalter iC60L, 3p, 16A, MA Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 1,6A, MA Charakt eristik","A9F90372",null,"Schneider",1.6,2.6,null,null,2.6,"Leitungsschutzschalter iC60L, 3p, 1,6A, MA Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 2,5A, MA Charakt eristik","A9F90373",null,"Schneider",2.5,2.2000000000000002,null,null,2.2000000000000002,"Leitungsschutzschalter iC60L, 3p, 2,5A, MA Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 6,3A, MA Charakt eristik","A9F90376",null,"Schneider",6.3,1.3,null,null,1.3,"Leitungsschutzschalter iC60L, 3p, 6,3A, MA Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 12,5A, MA Charak teristik","A9F90382",null,"Schneider",12.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 3p, 12,5A, MA Charak teristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 1p, 0,5A, Z Charakte ristik","A9F92170",null,"Schneider",0.5,2.2999999999999998,null,null,{"$f":"G1606+I1606","v":2.2999999999999998},"Leitungsschutzschalter iC60L, 1p, 0,5A, Z Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 1p, 1,6A, Z Charakte ristik","A9F92172",null,"Schneider",1.6,2.6,null,null,2.6,"Leitungsschutzschalter iC60L, 1p, 1,6A, Z Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 0,5A, Z Charakte ristik","A9F92270",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 2p, 0,5A, Z Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 1,6A, Z Charakte ristik","A9F92272",null,"Schneider",1.6,2.6,null,null,2.6,"Leitungsschutzschalter iC60L, 2p, 1,6A, Z Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 0,5A, Z Charakte ristik","A9F92370",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 3p, 0,5A, Z Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 1,6A, Z Charakte ristik","A9F92372",null,"Schneider",1.6,2.6,null,null,2.6,"Leitungsschutzschalter iC60L, 3p, 1,6A, Z Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 4p, 0,5A, Z Charakte ristik","A9F92470",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 4p, 0,5A, Z Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 4p, 1,6A, Z Charakte ristik","A9F92472",null,"Schneider",1.6,2.6,null,null,2.6,"Leitungsschutzschalter iC60L, 4p, 1,6A, Z Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 1p, 3A, B Charakteri stik","A9F93103",null,"Schneider",3,2.2000000000000002,null,null,2.2000000000000002,"Leitungsschutzschalter iC60L, 1p, 3A, B Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 1p, 0,5A, B Charakte ristik","A9F93170",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 1p, 0,5A, B Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 1A, B Charakteri stik","A9F93201",null,"Schneider",1,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 2p, 1A, B Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 3A, B Charakteri stik","A9F93203",null,"Schneider",3,2.2000000000000002,null,null,2.2000000000000002,"Leitungsschutzschalter iC60L, 2p, 3A, B Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 0,5A, B Charakte ristik","A9F93270",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 2p, 0,5A, B Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 1A, B Charakteri stik","A9F93301",null,"Schneider",1,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 3p, 1A, B Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 3A, B Charakteri stik","A9F93303",null,"Schneider",3,2.2000000000000002,null,null,2.2000000000000002,"Leitungsschutzschalter iC60L, 3p, 3A, B Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 4A, B Charakteri stik","A9F93304",null,"Schneider",4,2.4,null,null,2.4,"Leitungsschutzschalter iC60L, 3p, 4A, B Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 0,5A, B Charakte ristik","A9F93370",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 3p, 0,5A, B Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 4p, 1A, B Charakteri stik","A9F93401",null,"Schneider",1,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 4p, 1A, B Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 4p, 2A, B Charakteri stik","A9F93402",null,"Schneider",2,1.9,null,null,1.9,"Leitungsschutzschalter iC60L, 4p, 2A, B Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 4p, 3A, B Charakteri stik","A9F93403",null,"Schneider",3,2.2000000000000002,null,null,2.2000000000000002,"Leitungsschutzschalter iC60L, 4p, 3A, B Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 4p, 4A, B Charakteri stik","A9F93404",null,"Schneider",4,2.4,null,null,{"$f":"G1626+I1626","v":2.4},"Leitungsschutzschalter iC60L, 4p, 4A, B Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 4p, 0,5A, B Charakte ristik","A9F93470",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 4p, 0,5A, B Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 1p, 0,5A, C Charakte ristik","A9F94170",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 1p, 0,5A, C Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 0,5A, C Charakte ristik","A9F94270",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 2p, 0,5A, C Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 0,5A, C Charakte ristik","A9F94370",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 3p, 0,5A, C Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 4p, 0,5A, C Charakte ristik","A9F94470",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 4p, 0,5A, C Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 1p, 1A, K Charakteri stik","A9F95101",null,"Schneider",1,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 1p, 1A, K Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 1p, 2A, K Charakteri stik","A9F95102",null,"Schneider",2,1.9,null,null,1.9,"Leitungsschutzschalter iC60L, 1p, 2A, K Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 1p, 3A, K Charakteri stik","A9F95103",null,"Schneider",3,2.2000000000000002,null,null,2.2000000000000002,"Leitungsschutzschalter iC60L, 1p, 3A, K Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 1p, 4A, K Charakteri stik","A9F95104",null,"Schneider",4,2.4,null,null,2.4,"Leitungsschutzschalter iC60L, 1p, 4A, K Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 1p, 6A, K Charakteri stik","A9F95106",null,"Schneider",6,1.3,null,null,1.3,"Leitungsschutzschalter iC60L, 1p, 6A, K Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 1p, 10A, K Charakter istik","A9F95110",null,"Schneider",10,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 1p, 10A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 1p, 20A, K Charakter istik","A9F95120",null,"Schneider",20,2.4,null,null,2.4,"Leitungsschutzschalter iC60L, 1p, 20A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 1p, 25A, K Charakter istik","A9F95125",null,"Schneider",25,3,null,null,3,"Leitungsschutzschalter iC60L, 1p, 25A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 1p, 32A, K Charakter istik","A9F95132",null,"Schneider",32,2.8,null,null,2.8,"Leitungsschutzschalter iC60L, 1p, 32A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 1p, 40A, K Charakter istik","A9F95140",null,"Schneider",40,3.6,null,null,3.6,"Leitungsschutzschalter iC60L, 1p, 40A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 1p, 50A, K Charakter istik","A9F95150",null,"Schneider",50,4,null,null,4,"Leitungsschutzschalter iC60L, 1p, 50A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 1p, 63A, K Charakter istik","A9F95163",null,"Schneider",63,5.6,null,null,5.6,"Leitungsschutzschalter iC60L, 1p, 63A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 1p, 0,5A, K Charakte ristik","A9F95170",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 1p, 0,5A, K Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 1p, 1,6A, K Charakte ristik","A9F95172",null,"Schneider",1.6,2.6,null,null,2.6,"Leitungsschutzschalter iC60L, 1p, 1,6A, K Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 1A, K Charakteri stik","A9F95201",null,"Schneider",1,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 2p, 1A, K Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 2A, K Charakteri stik","A9F95202",null,"Schneider",2,1.9,null,null,1.9,"Leitungsschutzschalter iC60L, 2p, 2A, K Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 3A, K Charakteri stik","A9F95203",null,"Schneider",3,2.2000000000000002,null,null,2.2000000000000002,"Leitungsschutzschalter iC60L, 2p, 3A, K Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 4A, K Charakteri stik","A9F95204",null,"Schneider",4,2.4,null,null,2.4,"Leitungsschutzschalter iC60L, 2p, 4A, K Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 6A, K Charakteri stik","A9F95206",null,"Schneider",6,1.3,null,null,1.3,"Leitungsschutzschalter iC60L, 2p, 6A, K Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 10A, K Charakter istik","A9F95210",null,"Schneider",10,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 2p, 10A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 16A, K Charakter istik","A9F95216",null,"Schneider",16,2.4,null,null,2.4,"Leitungsschutzschalter iC60L, 2p, 16A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 20A, K Charakter istik","A9F95220",null,"Schneider",20,2.4,null,null,2.4,"Leitungsschutzschalter iC60L, 2p, 20A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 25A, K Charakter istik","A9F95225",null,"Schneider",25,3,null,null,3,"Leitungsschutzschalter iC60L, 2p, 25A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 32A, K Charakter istik","A9F95232",null,"Schneider",32,2.8,null,null,2.8,"Leitungsschutzschalter iC60L, 2p, 32A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 40A, K Charakter istik","A9F95240",null,"Schneider",40,3.6,null,null,3.6,"Leitungsschutzschalter iC60L, 2p, 40A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 50A, K Charakter istik","A9F95250",null,"Schneider",50,4,null,null,4,"Leitungsschutzschalter iC60L, 2p, 50A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 63A, K Charakter istik","A9F95263",null,"Schneider",63,5.6,null,null,5.6,"Leitungsschutzschalter iC60L, 2p, 63A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 0,5A, K Charakte ristik","A9F95270",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 2p, 0,5A, K Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 2p, 1,6A, K Charakte ristik","A9F95272",null,"Schneider",1.6,2.6,null,null,2.6,"Leitungsschutzschalter iC60L, 2p, 1,6A, K Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 1A, K Charakteri stik","A9F95301",null,"Schneider",1,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 3p, 1A, K Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 2A, K Charakteri stik","A9F95302",null,"Schneider",2,1.9,null,null,1.9,"Leitungsschutzschalter iC60L, 3p, 2A, K Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 3A, K Charakteri stik","A9F95303",null,"Schneider",3,2.2000000000000002,null,null,2.2000000000000002,"Leitungsschutzschalter iC60L, 3p, 3A, K Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 4A, K Charakteri stik","A9F95304",null,"Schneider",4,2.4,null,null,2.4,"Leitungsschutzschalter iC60L, 3p, 4A, K Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 6A, K Charakteri stik","A9F95306",null,"Schneider",6,1.3,null,null,1.3,"Leitungsschutzschalter iC60L, 3p, 6A, K Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 10A, K Charakter istik","A9F95310",null,"Schneider",10,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 3p, 10A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 16A, K Charakter istik","A9F95316",null,"Schneider",16,2.4,null,null,2.4,"Leitungsschutzschalter iC60L, 3p, 16A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 20A, K Charakter istik","A9F95320",null,"Schneider",20,2.4,null,null,2.4,"Leitungsschutzschalter iC60L, 3p, 20A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 25A, K Charakter istik","A9F95325",null,"Schneider",25,3,null,null,3,"Leitungsschutzschalter iC60L, 3p, 25A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 32A, K Charakter istik","A9F95332",null,"Schneider",32,2.8,null,null,2.8,"Leitungsschutzschalter iC60L, 3p, 32A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 40A, 20kA K Charakteristik","A9F95340",null,"Schneider",40,3.6,null,null,3.6,"Leitungsschutzschalter iC60L, 3p, 40A, 20kA K Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 50A, K Charakter istik","A9F95350",null,"Schneider",50,4,null,null,4,"Leitungsschutzschalter iC60L, 3p, 50A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 63A, K Charakter istik","A9F95363",null,"Schneider",63,5.6,null,null,5.6,"Leitungsschutzschalter iC60L, 3p, 63A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 0,5A, K Charakte ristik","A9F95370",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 3p, 0,5A, K Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 3p, 1,6A, K Charakte ristik","A9F95372",null,"Schneider",1.6,2.6,null,null,2.6,"Leitungsschutzschalter iC60L, 3p, 1,6A, K Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 4p, 1A, K Charakteri stik","A9F95401",null,"Schneider",1,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 4p, 1A, K Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 4p, 2A, K Charakteri stik","A9F95402",null,"Schneider",2,1.9,null,null,1.9,"Leitungsschutzschalter iC60L, 4p, 2A, K Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 4p, 3A, K Charakteri stik","A9F95403",null,"Schneider",3,2.2000000000000002,null,null,2.2000000000000002,"Leitungsschutzschalter iC60L, 4p, 3A, K Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 4p, 4A, K Charakteri stik","A9F95404",null,"Schneider",4,2.4,null,null,2.4,"Leitungsschutzschalter iC60L, 4p, 4A, K Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 4p, 6A, K Charakteri stik","A9F95406",null,"Schneider",6,1.3,null,null,1.3,"Leitungsschutzschalter iC60L, 4p, 6A, K Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 4p, 10A, K Charakter istik","A9F95410",null,"Schneider",10,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 4p, 10A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 4p, 16A, K Charakter istik","A9F95416",null,"Schneider",16,2.4,null,null,2.4,"Leitungsschutzschalter iC60L, 4p, 16A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 4p, 25A, K Charakter istik","A9F95425",null,"Schneider",25,3,null,null,3,"Leitungsschutzschalter iC60L, 4p, 25A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 4p, 32A, K Charakter istik","A9F95432",null,"Schneider",32,2.8,null,null,2.8,"Leitungsschutzschalter iC60L, 4p, 32A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 4p, 40A, K Charakter istik","A9F95440",null,"Schneider",40,3.6,null,null,3.6,"Leitungsschutzschalter iC60L, 4p, 40A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 4p, 50A, K Charakter istik","A9F95450",null,"Schneider",50,4,null,null,4,"Leitungsschutzschalter iC60L, 4p, 50A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 4p, 63A, K Charakter istik","A9F95463",null,"Schneider",63,5.6,null,null,5.6,"Leitungsschutzschalter iC60L, 4p, 63A, K Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 4p, 0,5A, K Charakte ristik","A9F95470",null,"Schneider",0.5,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter iC60L, 4p, 0,5A, K Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iC60L, 4p, 1,6A, K Charakte ristik","A9F95472",null,"Schneider",1.6,2.6,null,null,2.6,"Leitungsschutzschalter iC60L, 4p, 1,6A, K Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter Resi9  1P, 10A, B, 6kA","R9F23110",null,"Schneider",10,1.9,null,null,{"$f":"G1690+I1690","v":1.9},"Leitungsschutzschalter Resi9  1P, 10A, B, 6kA"]
["Leistungsschalter REG","Leitungsschutzschalter Resi9 1P, 13A, B Charakteristik, 6kA","R9F23113",null,"Schneider",13,2.4,null,null,2.4,"Leitungsschutzschalter Resi9 1P, 13A, B Charakteristik, 6kA"]
["Leistungsschalter REG","Leitungsschutzschalter Resi9  1P, 16A, B, 6kA","R9F23116",null,"Schneider",16,2.6,null,null,2.6,"Leitungsschutzschalter Resi9  1P, 16A, B, 6kA"]
["Leistungsschalter REG","Leitungsschutzschalter Resi9 1P, 20A, B Charakteristik, 6kA","R9F23120",null,"Schneider",20,2.2000000000000002,null,null,2.2000000000000002,"Leitungsschutzschalter Resi9 1P, 20A, B Charakteristik, 6kA"]
["Leistungsschalter REG","Leitungsschutzschalter Resi9 1P, 25A, B Charakteristik, 6kA","R9F23125",null,"Schneider",25,2.7,null,null,2.7,"Leitungsschutzschalter Resi9 1P, 25A, B Charakteristik, 6kA"]
["Leistungsschalter REG","Leitungsschutzschalter Resi9 1P, 32A, B Charakteristik, 6kA","R9F23132",null,"Schneider",32,3.2,null,null,3.2,"Leitungsschutzschalter Resi9 1P, 32A, B Charakteristik, 6kA"]
["Leistungsschalter REG","Leitungsschutzschalter Resi9 3P, 10A, B Charakteristik, 6kA","R9F23310",null,"Schneider",10,1.9,null,null,1.9,"Leitungsschutzschalter Resi9 3P, 10A, B Charakteristik, 6kA"]
["Leistungsschalter REG","Leitungsschutzschalter Resi9, 3P, 16A, B, 6kA","R9F23316",null,"Schneider",16,2.6,null,null,2.6,"Leitungsschutzschalter Resi9, 3P, 16A, B, 6kA"]
["Leistungsschalter REG","Leitungsschutzschalter Resi9 3P, 20A, B Charakteristik, 6kA","R9F23320",null,"Schneider",20,2.2000000000000002,null,null,2.2000000000000002,"Leitungsschutzschalter Resi9 3P, 20A, B Charakteristik, 6kA"]
["Leistungsschalter REG","Leitungsschutzschalter Resi9 3P, 25A, B Charakteristik, 6kA","R9F23325",null,"Schneider",25,2.7,null,null,2.7,"Leitungsschutzschalter Resi9 3P, 25A, B Charakteristik, 6kA"]
["Leistungsschalter REG","Leitungsschutzschalter Resi9 3P, 32A, B Charakteristik, 6kA","R9F23332",null,"Schneider",32,3.2,null,null,3.2,"Leitungsschutzschalter Resi9 3P, 32A, B Charakteristik, 6kA"]
["Leistungsschalter REG","Leitungsschutzschalter Resi9 1P, 10A, C Charakteristik, 6kA","R9F24110",null,"Schneider",10,1.9,null,null,1.9,"Leitungsschutzschalter Resi9 1P, 10A, C Charakteristik, 6kA"]
["Leistungsschalter REG","Leitungsschutzschalter Resi9 1P, 16A, C Charakteristik, 6kA","R9F24116",null,"Schneider",16,2.6,null,null,2.6,"Leitungsschutzschalter Resi9 1P, 16A, C Charakteristik, 6kA"]
["Leistungsschalter REG","Leitungsschutzschalter Resi9 3P, 16A, C Charakteristik, 6kA","R9F24316",null,"Schneider",16,2.6,null,null,2.6,"Leitungsschutzschalter Resi9 3P, 16A, C Charakteristik, 6kA"]
["Leistungsschalter REG","Leitungsschutzschalter Resi9 3P, 32A, C Charakteristik, 6kA","R9F24332",null,"Schneider",32,3.2,null,null,3.2,"Leitungsschutzschalter Resi9 3P, 32A, C Charakteristik, 6kA"]
["Leistungsschalter REG","Leitungsschutzschalter Resi9, 1P, 6A, B, 10kA","R9F27106",null,"Schneider",6,1.2,null,null,1.2,"Leitungsschutzschalter Resi9, 1P, 6A, B, 10kA"]
["Leistungsschalter REG","Leitungsschutzschalter Resi9 3P, 16A, B Charakteristik, 10kA","R9F27316",null,"Schneider",16,2.6,null,null,2.6,"Leitungsschutzschalter Resi9 3P, 16A, B Charakteristik, 10kA"]
["Leistungsschalter REG","Leitungsschutzschalter iDPN, 1p+N, 6A, C-Charakter istik","A9N21555",null,"Schneider",6,2.7,null,null,2.7,"Leitungsschutzschalter iDPN, 1p+N, 6A, C-Charakter istik"]
["Leistungsschalter REG","Leitungsschutzschalter iDPN, 1p+N, 10A, C-Charakte ristik","A9N21556",null,"Schneider",10,2.7,null,null,2.7,"Leitungsschutzschalter iDPN, 1p+N, 10A, C-Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iDPN, 1p+N, 16A, C-Charakte ristik","A9N21557",null,"Schneider",16,3.2,null,null,3.2,"Leitungsschutzschalter iDPN, 1p+N, 16A, C-Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter iDPN, 3p, 10A, C-Charakteri stik","A9N21576",null,"Schneider",10,2.7,null,null,2.7,"Leitungsschutzschalter iDPN, 3p, 10A, C-Charakteri stik"]
["Leistungsschalter REG","Leitungsschutzschalter iDPN, 3p+N, 16A,  C-Charakteristik","A9N21597",null,"Schneider",16,3.2,null,null,3.2,"Leitungsschutzschalter iDPN, 3p+N, 16A,  C-Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 1p, 0,5A Charakter istik C","A9N61500",null,"Schneider",0.5,2.2000000000000002,null,null,2.2000000000000002,"Leitungsschutzschalter C60H-DC, 1p, 0,5A Charakter istik C"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 1p, 1A, C Charakte ristik","A9N61501",null,"Schneider",1,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter C60H-DC, 1p, 1A, C Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 1p, 2A, C Charakte ristik","A9N61502",null,"Schneider",2,2.6,null,null,2.6,"Leitungsschutzschalter C60H-DC, 1p, 2A, C Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 1p, 3A, C Charakte ristik","A9N61503",null,"Schneider",3,2.2000000000000002,null,null,2.2000000000000002,"Leitungsschutzschalter C60H-DC, 1p, 3A, C Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 1p, 4A, C Charakte ristik","A9N61504",null,"Schneider",4,2.4,null,null,2.4,"Leitungsschutzschalter C60H-DC, 1p, 4A, C Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 1p, 5A, C Charakte ristik","A9N61505",null,"Schneider",5,2.7,null,null,2.7,"Leitungsschutzschalter C60H-DC, 1p, 5A, C Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 1p, 6A, C Charakte ristik","A9N61506",null,"Schneider",6,2.7,null,null,2.7,"Leitungsschutzschalter C60H-DC, 1p, 6A, C Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 1p, 10A, C Charakt eristik","A9N61508",null,"Schneider",10,1.8,null,null,1.8,"Leitungsschutzschalter C60H-DC, 1p, 10A, C Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 1p, 13A, C Charakt eristik","A9N61509",null,"Schneider",13,2.5,null,null,2.5,"Leitungsschutzschalter C60H-DC, 1p, 13A, C Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 1p, 15A, C Charakt eristik","A9N61510",null,"Schneider",15,2.5,null,null,2.5,"Leitungsschutzschalter C60H-DC, 1p, 15A, C Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 1p, 16A, C Charakt eristik","A9N61511",null,"Schneider",16,2.5,null,null,2.5,"Leitungsschutzschalter C60H-DC, 1p, 16A, C Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 1p, 20A, C Charakt eristik","A9N61512",null,"Schneider",20,3,null,null,3,"Leitungsschutzschalter C60H-DC, 1p, 20A, C Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 1p, 25A, C Charakt eristik","A9N61513",null,"Schneider",25,3.1,null,null,3.1,"Leitungsschutzschalter C60H-DC, 1p, 25A, C Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 1p, 30A, C Charakt eristik","A9N61514",null,"Schneider",30,3.5,null,null,3.5,"Leitungsschutzschalter C60H-DC, 1p, 30A, C Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 1p, 32A, C Charakt eristik","A9N61515",null,"Schneider",32,3.5,null,null,3.5,"Leitungsschutzschalter C60H-DC, 1p, 32A, C Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 1p, 40A, C Charakt eristik","A9N61517",null,"Schneider",40,3.6,null,null,3.6,"Leitungsschutzschalter C60H-DC, 1p, 40A, C Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 1p, 50A, C Charakt eristik","A9N61518",null,"Schneider",50,4,null,null,4,"Leitungsschutzschalter C60H-DC, 1p, 50A, C Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 1p, 63A, C Charakt eristik","A9N61519",null,"Schneider",63,5.6,null,null,5.6,"Leitungsschutzschalter C60H-DC, 1p, 63A, C Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 2p, 0,5A, C Charak teristik","A9N61520",null,"Schneider",0.5,2.2000000000000002,null,null,2.2000000000000002,"Leitungsschutzschalter C60H-DC, 2p, 0,5A, C Charak teristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 2p, 1A, C Charakte ristik","A9N61521",null,"Schneider",1,2.2999999999999998,null,null,2.2999999999999998,"Leitungsschutzschalter C60H-DC, 2p, 1A, C Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 2p, 2A, C Charakte ristik","A9N61522",null,"Schneider",2,2.6,null,null,2.6,"Leitungsschutzschalter C60H-DC, 2p, 2A, C Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 2p, 3A, C Charakte ristik","A9N61523",null,"Schneider",3,2.2000000000000002,null,null,2.2000000000000002,"Leitungsschutzschalter C60H-DC, 2p, 3A, C Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 2p, 4A, C Charakte ristik","A9N61524",null,"Schneider",4,2.4,null,null,2.4,"Leitungsschutzschalter C60H-DC, 2p, 4A, C Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 2p, 5A, C Charakte ristik","A9N61525",null,"Schneider",5,2.7,null,null,2.7,"Leitungsschutzschalter C60H-DC, 2p, 5A, C Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 2p, 6A, C Charakte ristik","A9N61526",null,"Schneider",6,2.7,null,null,2.7,"Leitungsschutzschalter C60H-DC, 2p, 6A, C Charakte ristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 2p, 10A, C Charakt eristik","A9N61528",null,"Schneider",10,1.8,null,null,1.8,"Leitungsschutzschalter C60H-DC, 2p, 10A, C Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 2p, 13A, C Charakt eristik","A9N61529",null,"Schneider",13,2.5,null,null,2.5,"Leitungsschutzschalter C60H-DC, 2p, 13A, C Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 2p, 15A, C Charakt eristik","A9N61530",null,"Schneider",15,2.5,null,null,2.5,"Leitungsschutzschalter C60H-DC, 2p, 15A, C Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 2p, 16A, C Charakt eristik","A9N61531",null,"Schneider",16,2.5,null,null,2.5,"Leitungsschutzschalter C60H-DC, 2p, 16A, C Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 2p, 20A, C Charakt eristik","A9N61532",null,"Schneider",20,3,null,null,3,"Leitungsschutzschalter C60H-DC, 2p, 20A, C Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 2p, 25A, C Charakt eristik","A9N61533",null,"Schneider",25,3.1,null,null,3.1,"Leitungsschutzschalter C60H-DC, 2p, 25A, C Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 2p, 30A, C Charakt eristik","A9N61534",null,"Schneider",30,3.5,null,null,3.5,"Leitungsschutzschalter C60H-DC, 2p, 30A, C Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 2p, 32A, C Charakt eristik","A9N61535",null,"Schneider",32,3.5,null,null,3.5,"Leitungsschutzschalter C60H-DC, 2p, 32A, C Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 2p, 40A, C Charakt eristik","A9N61537",null,"Schneider",40,3.6,null,null,3.6,"Leitungsschutzschalter C60H-DC, 2p, 40A, C Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 2p, 50A, C Charakt eristik","A9N61538",null,"Schneider",50,4,null,null,4,"Leitungsschutzschalter C60H-DC, 2p, 50A, C Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60H-DC, 2p, 63A, C Charakt eristik","A9N61539",null,"Schneider",63,5.6,null,null,5.6,"Leitungsschutzschalter C60H-DC, 2p, 63A, C Charakt eristik"]
["Leistungsschalter REG","Leitungsschutzschalter C60pV-DC, 2p, 800V DC, 10A","A9N61650",null,"Schneider",10,6.8,null,null,6.8,"Leitungsschutzschalter C60pV-DC, 2p, 800V DC, 10A"]
["Leistungsschalter REG","Leitungsschutzschalter C60pV-DC, 2p, 800V DC, 16A","A9N61651",null,"Schneider",16,10.4,null,null,10.4,"Leitungsschutzschalter C60pV-DC, 2p, 800V DC, 16A"]
["Leistungsschalter REG","Leitungsschutzschalter C60pV-DC, 2p, 800V DC, 20A","A9N61652",null,"Schneider",20,11.8,null,null,11.8,"Leitungsschutzschalter C60pV-DC, 2p, 800V DC, 20A"]
["Leistungsschalter REG","Leitungsschutzschalter C60pV-DC, 2p, 800V DC, 2A","A9N61654",null,"Schneider",2,10.199999999999999,null,null,10.199999999999999,"Leitungsschutzschalter C60pV-DC, 2p, 800V DC, 2A"]
["Leistungsschalter REG","Leitungsschutzschalter C60pV-DC, 2p, 800V DC, 3A","A9N61655",null,"Schneider",3,8.9,null,null,8.9,"Leitungsschutzschalter C60pV-DC, 2p, 800V DC, 3A"]
["Leistungsschalter REG","Leitungsschutzschalter C60pV-DC, 2p, 800V DC, 13A","A9N61658",null,"Schneider",13,7.4,null,null,7.4,"Leitungsschutzschalter C60pV-DC, 2p, 800V DC, 13A"]
["Leistungsschalter REG","Leitungsschutzschalter C60pV-DC, 2p, 800V DC, 25A","A9N61660",null,"Schneider",25,12.2,null,null,{"$f":"G1754+I1754","v":12.2},"Leitungsschutzschalter C60pV-DC, 2p, 800V DC, 25A"]
["Leistungsschalter REG","Leitungsschutzschalter iDPN, 1p+N, 10A,  B Charakteristik","A9N17517",null,"Schneider",10,2.7,null,null,2.7,"Leitungsschutzschalter iDPN, 1p+N, 10A,  B Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter iDPN, 1p+N, 13A,  B Charakteristik","A9N17518",null,"Schneider",13,3.3,null,null,3.3,"Leitungsschutzschalter iDPN, 1p+N, 13A,  B Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter iDPN, 1p+N, 16A,  B Charakteristik","A9N17519",null,"Schneider",16,3.2,null,null,3.2,"Leitungsschutzschalter iDPN, 1p+N, 16A,  B Charakteristik"]
["Leistungsschalter REG","C40N, Leitungsschalter, 3p+N, 10A, B-Kurve","A9N17554",null,"Schneider",10,6.8,null,null,6.8,"C40N, Leitungsschalter, 3p+N, 10A, B-Kurve"]
["Leistungsschalter REG","Leitungsschutzschalter iDPN, 3p+N, 16A, B Charakteristik","A9N17555",null,"Schneider",16,3.2,null,null,3.2,"Leitungsschutzschalter iDPN, 3p+N, 16A, B Charakteristik"]
["Leistungsschalter REG","Leitungsschutzschalter iDPN, 3p+N, 32A,  B Charakteristik","A9N17558",null,"Schneider",32,4.5999999999999996,null,null,4.5999999999999996,"Leitungsschutzschalter iDPN, 3p+N, 32A,  B Charakteristik"]
[]
["Lasttrennschalter REG","LasttrennschalteriSW, 1p, 20A, 250V","A9S60120",null,"Schneider",20,0.8,null,null,{"$f":"G1762+I1762","v":0.8},"LasttrennschalteriSW, 1p, 20A, 250V"]
["Lasttrennschalter REG","Lasttrennschalter iSW mit Leuchtmelder, 1p, 20A 250V","A9S61120",null,"Schneider",20,0.8,null,null,0.8,"Lasttrennschalter iSW mit Leuchtmelder, 1p, 20A 250V"]
["Lasttrennschalter REG","Lasttrennschalter iSW mit Leuchtmelder, 2p 20A, 250V","A9S61220",null,"Schneider",20,0.8,null,null,0.8,"Lasttrennschalter iSW mit Leuchtmelder, 2p 20A, 250V"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 1p, 40A, 240V AC","A9S65140",null,"Schneider",40,0.6,null,null,0.6,"Lasttrennschalter iSW, 1p, 40A, 240V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 3p, 63A, 415V AC","A9S65363",null,"Schneider",63,1.8,null,null,1.8,"Lasttrennschalter iSW, 3p, 63A, 415V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 3p, 100A, 415V AC","A9S65391",null,"Schneider",100,4.7,null,null,4.7,"Lasttrennschalter iSW, 3p, 100A, 415V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 3p, 125A, 415V AC","A9S65392",null,"Schneider",125,6.4,null,null,6.4,"Lasttrennschalter iSW, 3p, 125A, 415V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 4p, 40A, 415V AC","A9S65440",null,"Schneider",40,0.6,null,null,0.6,"Lasttrennschalter iSW, 4p, 40A, 415V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 4p, 63A, 415V AC","A9S65463",null,"Schneider",63,1.8,null,null,1.8,"Lasttrennschalter iSW, 4p, 63A, 415V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 4p, 100A, 415V AC","A9S65491",null,"Schneider",100,4.7,null,null,4.7,"Lasttrennschalter iSW, 4p, 100A, 415V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 4p, 125A, 415V AC","A9S65492",null,"Schneider",125,6.4,null,null,6.4,"Lasttrennschalter iSW, 4p, 125A, 415V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 3p, 63A, 240V AC","A9S66363",null,"Schneider",63,1.8,null,null,1.8,"Lasttrennschalter iSW, 3p, 63A, 240V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 3p, 100A, 415V AC","A9S66391",null,"Schneider",100,4.7,null,null,4.7,"Lasttrennschalter iSW, 3p, 100A, 415V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 3p, 125A, 415V AC Knebel rot","A9S66392",null,"Schneider",125,6.4,null,null,6.4,"Lasttrennschalter iSW, 3p, 125A, 415V AC Knebel rot"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 4p, 100A, 415V AC","A9S66491",null,"Schneider",100,4.7,null,null,4.7,"Lasttrennschalter iSW, 4p, 100A, 415V AC"]
["Lasttrennschalter REG","Lasttrennschalter C60NA-DC, 2p, 1000V DC","A9N61690",null,"Schneider",50,12.6,null,null,12.6,"Lasttrennschalter C60NA-DC, 2p, 1000V DC"]
["Lasttrennschalter REG","Lasttrennschalter SW60-DC, 2p, 1000V DC","A9N61699",null,"Schneider",50,12.6,null,null,12.6,"Lasttrennschalter SW60-DC, 2p, 1000V DC"]
["Lasttrennschalter REG","LASTTRENNSCH. C120NA-DC 1000 VDC 100A 2P","A9N61701",null,"Schneider",100,8,null,null,8,"LASTTRENNSCH. C120NA-DC 1000 VDC 100A 2P"]
["Lasttrennschalter REG","LasttrennschalteriSW, 1p, 32A, 250V","A9S60132",null,"Schneider",32,0.7,null,null,0.7,"LasttrennschalteriSW, 1p, 32A, 250V"]
["Lasttrennschalter REG","LasttrennschalteriSW, 2p, 20A, 415V","A9S60220",null,"Schneider",32,0.7,null,null,0.7,"LasttrennschalteriSW, 2p, 20A, 415V"]
["Lasttrennschalter REG","LasttrennschalteriSW, 2p, 32A, 415V","A9S60232",null,"Schneider",20,0.7,null,null,0.7,"LasttrennschalteriSW, 2p, 32A, 415V"]
["Lasttrennschalter REG","LasttrennschalteriSW, 3p, 32A, 415V","A9S60332",null,"Schneider",32,0.7,null,null,0.7,"LasttrennschalteriSW, 3p, 32A, 415V"]
["Lasttrennschalter REG","LasttrennschalteriSW, 4p, 20A, 415V","A9S60420",null,"Schneider",20,0.7,null,null,0.7,"LasttrennschalteriSW, 4p, 20A, 415V"]
["Lasttrennschalter REG","LasttrennschalteriSW, 4p, 32A, 415V","A9S60432",null,"Schneider",32,0.7,null,null,0.7,"LasttrennschalteriSW, 4p, 32A, 415V"]
["Lasttrennschalter REG","Lasttrennschalter iSW mit Leuchtmelder, 1p, 32 A, 250V","A9S61132",null,"Schneider",32,0.7,null,null,0.7,"Lasttrennschalter iSW mit Leuchtmelder, 1p, 32 A, 250V"]
["Lasttrennschalter REG","Lasttrennschalter iSW mit Leuchtmelder, 2p, 32 A, 250V","A9S61232",null,"Schneider",32,0.7,null,null,0.7,"Lasttrennschalter iSW mit Leuchtmelder, 2p, 32 A, 250V"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 1p, 63A, 240V AC","A9S65163",null,"Schneider",63,1.8,null,null,1.8,"Lasttrennschalter iSW, 1p, 63A, 240V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 1p, 100A, 240V AC","A9S65191",null,"Schneider",100,4.7,null,null,4.7,"Lasttrennschalter iSW, 1p, 100A, 240V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 1p, 125A, 240V AC","A9S65192",null,"Schneider",125,6.4,null,null,6.4,"Lasttrennschalter iSW, 1p, 125A, 240V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 2p, 40A, 415V AC","A9S65240",null,"Schneider",40,0.6,null,null,0.6,"Lasttrennschalter iSW, 2p, 40A, 415V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 2p, 63A, 415V AC","A9S65263",null,"Schneider",63,1.8,null,null,1.8,"Lasttrennschalter iSW, 2p, 63A, 415V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 2p, 100A, 415V AC","A9S65291",null,"Schneider",100,4.7,null,null,4.7,"Lasttrennschalter iSW, 2p, 100A, 415V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 2p, 125A, 415V AC","A9S65292",null,"Schneider",125,6.4,null,null,{"$f":"G1794+I1794","v":6.4},"Lasttrennschalter iSW, 2p, 125A, 415V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 3p, 40A, 415V AC","A9S65340",null,"Schneider",40,0.6,null,null,0.6,"Lasttrennschalter iSW, 3p, 40A, 415V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 1p, 40A, 240V AC","A9S66140",null,"Schneider",40,0.6,null,null,0.6,"Lasttrennschalter iSW, 1p, 40A, 240V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 1p, 63A, 240V AC","A9S66163",null,"Schneider",63,1.8,null,null,1.8,"Lasttrennschalter iSW, 1p, 63A, 240V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 1p, 100A, 240V AC","A9S66191",null,"Schneider",100,4.7,null,null,4.7,"Lasttrennschalter iSW, 1p, 100A, 240V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 1p, 125A, 240V AC","A9S66192",null,"Schneider",125,6.4,null,null,6.4,"Lasttrennschalter iSW, 1p, 125A, 240V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 2p, 40A, 415V AC","A9S66240",null,"Schneider",40,0.6,null,null,0.6,"Lasttrennschalter iSW, 2p, 40A, 415V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 2p, 63A, 415V AC","A9S66263",null,"Schneider",63,1.8,null,null,1.8,"Lasttrennschalter iSW, 2p, 63A, 415V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 2p, 100A, 415V AC","A9S66291",null,"Schneider",100,4.7,null,null,4.7,"Lasttrennschalter iSW, 2p, 100A, 415V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 2p, 125A, 415V AC","A9S66292",null,"Schneider",125,6.4,null,null,6.4,"Lasttrennschalter iSW, 2p, 125A, 415V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 3p, 40A, 415V AC","A9S66340",null,"Schneider",40,0.6,null,null,0.6,"Lasttrennschalter iSW, 3p, 40A, 415V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 4p, 40A, 415V AC","A9S66440",null,"Schneider",40,0.6,null,null,0.6,"Lasttrennschalter iSW, 4p, 40A, 415V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 4p, 63A, 415V AC","A9S66463",null,"Schneider",63,1.8,null,null,1.8,"Lasttrennschalter iSW, 4p, 63A, 415V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW, 4p, 125A, 415V AC","A9S66492",null,"Schneider",125,6.4,null,null,6.4,"Lasttrennschalter iSW, 4p, 125A, 415V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW-NA, 1p+N, 40A, 230-240V AC","A9S70640",null,"Schneider",40,0.7,null,null,0.7,"Lasttrennschalter iSW-NA, 1p+N, 40A, 230-240V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW-NA, 1p+N, 63A, 230-240V AC","A9S70663",null,"Schneider",63,1.8,null,null,1.8,"Lasttrennschalter iSW-NA, 1p+N, 63A, 230-240V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW-NA, 1p+N, 100A, 230-240V AC","A9S70690",null,"Schneider",100,3,null,null,3,"Lasttrennschalter iSW-NA, 1p+N, 100A, 230-240V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW-NA, 3p+N, 40A, 400-415V AC","A9S70740",null,"Schneider",40,0.7,null,null,0.7,"Lasttrennschalter iSW-NA, 3p+N, 40A, 400-415V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW-NA, 3p+N, 63A, 400-415V AC","A9S70763",null,"Schneider",63,1.8,null,null,1.8,"Lasttrennschalter iSW-NA, 3p+N, 63A, 400-415V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW-NA, 3p+N, 80A, 400-415V AC","A9S70780",null,"Schneider",80,3,null,null,3,"Lasttrennschalter iSW-NA, 3p+N, 80A, 400-415V AC"]
["Lasttrennschalter REG","Lasttrennschalter iSW-NA, 3p+N, 100A, 400-415V AC","A9S70790",null,"Schneider",100,3,null,null,3,"Lasttrennschalter iSW-NA, 3p+N, 100A, 400-415V AC"]
["Lasttrennschalter REG","Lasttrennschalter Resi9 3P, 63A, 415V AC","R9S64363",null,"Schneider",63,4.4000000000000004,null,null,4.4000000000000004,"Lasttrennschalter Resi9 3P, 63A, 415V AC"]
[null,null,null,null,null,null,null,null,null,0]
["Installationsschütz","Installationsschütz",null,"Verlustleistung Steuerkreis",null,null,"Verlustleistung Stromkreis ",null,null,null,"Installationsschütz"]
["Installationsschütz","Installationsschütz iCT 16A 1S 12V 50Hz","A9C22011",1.3,"Schneider",16,0.6,null,null,0.6,"Installationsschütz iCT 16A 1S 12V 50Hz"]
["Installationsschütz","Installationsschütz iCT 16A 1S 24V 50Hz","A9C22111",1.3,"Schneider",16,0.6,null,null,0.6,"Installationsschütz iCT 16A 1S 24V 50Hz"]
["Installationsschütz","Installationsschütz iCT 16A 1S 48V 50Hz","A9C22211",1.3,"Schneider",16,0.6,null,null,0.6,"Installationsschütz iCT 16A 1S 48V 50Hz"]
["Installationsschütz","Installationsschütz iCT 16A 1S 220V 50Hz","A9C22511",1.3,"Schneider",16,0.6,null,null,0.6,"Installationsschütz iCT 16A 1S 220V 50Hz"]
["Installationsschütz","Installationsschütz iCT 16A 1S 230/240V 50Hz","A9C22711",0.9,"Schneider",16,0.6,null,null,0.6,"Installationsschütz iCT 16A 1S 230/240V 50Hz"]
["Installationsschütz","Installationsschütz iCT 16A 2S 12V 50Hz","A9C22012",1.3,"Schneider",16,0.6,null,null,0.6,"Installationsschütz iCT 16A 2S 12V 50Hz"]
["Installationsschütz","Installationsschütz iCT 16A 2S 24V 50Hz","A9C22112",1.3,"Schneider",16,0.6,null,null,0.6,"Installationsschütz iCT 16A 2S 24V 50Hz"]
["Installationsschütz","Installationsschütz iCT 16A 2S 48V 50Hz","A9C22212",1.3,"Schneider",16,0.6,null,null,0.6,"Installationsschütz iCT 16A 2S 48V 50Hz"]
["Installationsschütz","Installationsschütz iCT 16A 2S 220V 50Hz","A9C22512",1.3,"Schneider",16,0.6,null,null,0.6,"Installationsschütz iCT 16A 2S 220V 50Hz"]
["Installationsschütz","Installationsschütz iCT 16A 2S 230/240V 50Hz","A9C22712",0.9,"Schneider",16,0.6,null,null,0.6,"Installationsschütz iCT 16A 2S 230/240V 50Hz"]
["Installationsschütz","Installationsschütz iCT 16A 2S 220V 50Hz MO","A9C23512",0.9,"Schneider",16,0.6,null,null,0.6,"Installationsschütz iCT 16A 2S 220V 50Hz MO"]
["Installationsschütz","Installationsschütz iCT 16A 2S 230/240V 50Hz MO","A9C23712",0.9,"Schneider",16,0.6,null,null,0.6,"Installationsschütz iCT 16A 2S 230/240V 50Hz MO"]
["Installationsschütz","Installationsschütz iCT 16A 1S 1Ö 12V 50Hz","A9C22015",1.3,"Schneider",16,0.6,null,null,0.6,"Installationsschütz iCT 16A 1S 1Ö 12V 50Hz"]
["Installationsschütz","Installationsschütz iCT 16A 1S 1Ö 24V AC 50Hz","A9C22115",1.3,"Schneider",16,0.6,null,null,0.6,"Installationsschütz iCT 16A 1S 1Ö 24V AC 50Hz"]
["Installationsschütz","Installationsschütz iCT 16A 1S 1Ö 220V 50Hz","A9C22515",1.3,"Schneider",16,0.6,null,null,0.6,"Installationsschütz iCT 16A 1S 1Ö 220V 50Hz"]
["Installationsschütz","Installationsschütz iCT 16A 1S 1Ö 220/240V 60Hz","A9C22615",0.9,"Schneider",16,0.6,null,null,0.6,"Installationsschütz iCT 16A 1S 1Ö 220/240V 60Hz"]
["Installationsschütz","Installationsschütz iCT 16A 1S 1Ö 230/240V 50Hz","A9C22715",0.9,"Schneider",16,0.6,null,null,0.6,"Installationsschütz iCT 16A 1S 1Ö 230/240V 50Hz"]
["Installationsschütz","Installationsschütz iCT 16A 1S 1Ö 220V 50Hz MO","A9C23515",1.3,"Schneider",16,0.6,null,null,0.6,"Installationsschütz iCT 16A 1S 1Ö 220V 50Hz MO"]
["Installationsschütz","Installationsschütz iCT 16A 1S 1Ö 230/240V 50Hz MO","A9C23715",0.9,"Schneider",16,0.6,null,null,0.6,"Installationsschütz iCT 16A 1S 1Ö 230/240V 50Hz MO"]
["Installationsschütz","Installationsschütz iCT 16A 3S 230/240V 50Hz","A9C22813",1.6,"Schneider",16,0.6,null,null,0.6,"Installationsschütz iCT 16A 3S 230/240V 50Hz"]
["Installationsschütz","Installationsschütz iCT 16A 4S 24V 50Hz","A9C22114",1.6,"Schneider",16,0.6,null,null,0.6,"Installationsschütz iCT 16A 4S 24V 50Hz"]
["Installationsschütz","Installationsschütz iCT 16A 4S 220/240V 50Hz","A9C22814",1.6,"Schneider",16,0.6,null,null,0.6,"Installationsschütz iCT 16A 4S 220/240V 50Hz"]
["Installationsschütz","Installationsschütz iCT 16A 2S 2Ö 220/240V 50Hz","A9C22818",1.6,"Schneider",16,0.6,null,null,0.6,"Installationsschütz iCT 16A 2S 2Ö 220/240V 50Hz"]
["Installationsschütz","Installationsschütz iCT 20A 2S 230/240V 50Hz","A9C22722",0.9,"Schneider",20,0.9,null,null,0.9,"Installationsschütz iCT 20A 2S 230/240V 50Hz"]
["Installationsschütz","Installationsschütz iCT 20A 4S 220/240V 50Hz","A9C22824",1.6,"Schneider",20,0.9,null,null,0.9,"Installationsschütz iCT 20A 4S 220/240V 50Hz"]
["Installationsschütz","Installationsschütz iCT 25A 1S 220V 50Hz","A9C20531",1.3,"Schneider",25,1.4,null,null,{"$f":"G1843+I1843","v":1.4},"Installationsschütz iCT 25A 1S 220V 50Hz"]
["Installationsschütz","Installationsschütz iCT 25A 1S 220/240V 60Hz","A9C20631",0.9,"Schneider",25,1.4,null,null,1.4,"Installationsschütz iCT 25A 1S 220/240V 60Hz"]
["Installationsschütz","Installationsschütz iCT 25A 1S 230/240V 50Hz","A9C20731",0.9,"Schneider",25,1.4,null,null,1.4,"Installationsschütz iCT 25A 1S 230/240V 50Hz"]
["Installationsschütz","Installationsschütz iCT 25A 2S 24V 50Hz","A9C20132",1.3,"Schneider",25,1.4,null,null,1.4,"Installationsschütz iCT 25A 2S 24V 50Hz"]
["Installationsschütz","Installationsschütz iCT 25A 2S 48V 50Hz","A9C20232",1.3,"Schneider",25,1.4,null,null,1.4,"Installationsschütz iCT 25A 2S 48V 50Hz"]
["Installationsschütz","Installationsschütz iCT 25A 2S 220V 50Hz","A9C20532",1.3,"Schneider",25,1.4,null,null,1.4,"Installationsschütz iCT 25A 2S 220V 50Hz"]
["Installationsschütz","Installationsschütz iCT 25A 2S 220/240V 60Hz","A9C20632",0.9,"Schneider",25,1.4,null,null,1.4,"Installationsschütz iCT 25A 2S 220/240V 60Hz"]
["Installationsschütz","Installationsschütz iCT 25A 2S 230/240V 50Hz","A9C20732",0.9,"Schneider",25,1.4,null,null,1.4,"Installationsschütz iCT 25A 2S 230/240V 50Hz"]
["Installationsschütz","Installationsschütz iCT 25A 2S 24V 50Hz MO","A9C21132",1.3,"Schneider",25,1.4,null,null,1.4,"Installationsschütz iCT 25A 2S 24V 50Hz MO"]
["Installationsschütz","Installationsschütz iCT 25A 2S 220V 50Hz MO","A9C21532",0.9,"Schneider",25,1.4,null,null,1.4,"Installationsschütz iCT 25A 2S 220V 50Hz MO"]
["Installationsschütz","Installationsschütz iCT 25A 2S 230/240V 50Hz MO","A9C21732",0.9,"Schneider",25,1.4,null,null,1.4,"Installationsschütz iCT 25A 2S 230/240V 50Hz MO"]
["Installationsschütz","Installationsschütz iCT 25A 2Ö 220/240V 60Hz","A9C20636",0.9,"Schneider",25,1.4,null,null,1.4,"Installationsschütz iCT 25A 2Ö 220/240V 60Hz"]
["Installationsschütz","Installationsschütz iCT 25A 2Ö 230/240V 50Hz","A9C20736",0.9,"Schneider",25,1.4,null,null,1.4,"Installationsschütz iCT 25A 2Ö 230/240V 50Hz"]
["Installationsschütz","Installationsschütz iCT 25A 2Ö 220V 50Hz","A9C20536",1.3,"Schneider",25,1.4,null,null,1.4,"Installationsschütz iCT 25A 2Ö 220V 50Hz"]
["Installationsschütz","Installationsschütz iCT 25A 3S 220/240V 60Hz","A9C20633",1.6,"Schneider",25,1.4,null,null,1.4,"Installationsschütz iCT 25A 3S 220/240V 60Hz"]
["Installationsschütz","Installationsschütz iCT 25A 3S 220/240V 50Hz","A9C20833",1.6,"Schneider",25,1.4,null,null,1.4,"Installationsschütz iCT 25A 3S 220/240V 50Hz"]
["Installationsschütz","Installationsschütz iCT 25A 3S 220/240V 50Hz MO","A9C21833",1.6,"Schneider",25,1.4,null,null,1.4,"Installationsschütz iCT 25A 3S 220/240V 50Hz MO"]
["Installationsschütz","Installationsschütz iCT 25A 4S 24V AC 50Hz","A9C20134",1.6,"Schneider",25,1.4,null,null,1.4,"Installationsschütz iCT 25A 4S 24V AC 50Hz"]
["Installationsschütz","Installationsschütz iCT 25A 4Ö 24V 50Hz","A9C20137",1.6,"Schneider",25,1.4,null,null,1.4,"Installationsschütz iCT 25A 4Ö 24V 50Hz"]
["Installationsschütz","Installationsschütz iCT 25A 4S 220/240V 50Hz","A9C20834",1.6,"Schneider",25,1.4,null,null,1.4,"Installationsschütz iCT 25A 4S 220/240V 50Hz"]
["Installationsschütz","Installationsschütz iCT 25A 4Ö 220/240V 50Hz","A9C20837",1.6,"Schneider",25,1.4,null,null,1.4,"Installationsschütz iCT 25A 4Ö 220/240V 50Hz"]
["Installationsschütz","Installationsschütz iCT 25A 2S 2Ö 220/240V 50Hz","A9C20838",1.6,"Schneider",25,1.4,null,null,1.4,"Installationsschütz iCT 25A 2S 2Ö 220/240V 50Hz"]
["Installationsschütz","Installationsschütz iCT 25A 4S 24V 50Hz MO","A9C21134",1.6,"Schneider",25,1.4,null,null,1.4,"Installationsschütz iCT 25A 4S 24V 50Hz MO"]
["Installationsschütz","Installationsschütz iCT 25A 4S 220/240V 50Hz MO","A9C21834",1.6,"Schneider",25,1.4,null,null,1.4,"Installationsschütz iCT 25A 4S 220/240V 50Hz MO"]
["Installationsschütz","Installationsschütz iCT 40A 2S 220/240V 60Hz","A9C20642",1.6,"Schneider",40,3.5,null,null,3.5,"Installationsschütz iCT 40A 2S 220/240V 60Hz"]
["Installationsschütz","Installationsschütz iCT 40A 2S 220/240 V 50Hz","A9C20842",1.6,"Schneider",40,3.5,null,null,3.5,"Installationsschütz iCT 40A 2S 220/240 V 50Hz"]
["Installationsschütz","Installationsschütz iCT 40A 2S 24V 50Hz MO","A9C21142",1.6,"Schneider",40,3.5,null,null,3.5,"Installationsschütz iCT 40A 2S 24V 50Hz MO"]
["Installationsschütz","Installationsschütz iCT 40A 2S 220/240V 60Hz MO","A9C21642",1.6,"Schneider",40,3.5,null,null,3.5,"Installationsschütz iCT 40A 2S 220/240V 60Hz MO"]
["Installationsschütz","Installationsschütz iCT 40A 2S 220/240V 50Hz MO","A9C21842",1.6,"Schneider",40,3.5,null,null,3.5,"Installationsschütz iCT 40A 2S 220/240V 50Hz MO"]
["Installationsschütz","Installationsschütz iCT 40A 3S 220/240V 60Hz","A9C20643",2.1,"Schneider",40,3.5,null,null,3.5,"Installationsschütz iCT 40A 3S 220/240V 60Hz"]
["Installationsschütz","Installationsschütz iCT 40A 3S 220/240 V 50Hz","A9C20843",2.1,"Schneider",40,3.5,null,null,3.5,"Installationsschütz iCT 40A 3S 220/240 V 50Hz"]
["Installationsschütz","Installationsschütz iCT 40A 3S 220/240V 50Hz MO","A9C21843",2.1,"Schneider",40,3.5,null,null,3.5,"Installationsschütz iCT 40A 3S 220/240V 50Hz MO"]
["Installationsschütz","Installationsschütz iCT 40A 4S 24V 50Hz MO","A9C21144",2.1,"Schneider",40,3.5,null,null,3.5,"Installationsschütz iCT 40A 4S 24V 50Hz MO"]
["Installationsschütz","Installationsschütz iCT 40A 4S 220/240 V 50Hz","A9C20844",2.1,"Schneider",40,3.5,null,null,3.5,"Installationsschütz iCT 40A 4S 220/240 V 50Hz"]
["Installationsschütz","Installationsschütz iCT 40A 4Ö 220/240V 50Hz","A9C20847",2.1,"Schneider",40,3.5,null,null,3.5,"Installationsschütz iCT 40A 4Ö 220/240V 50Hz"]
["Installationsschütz","Installationsschütz iCT 40A 4S 220/240V 50Hz MO","A9C21844",2.1,"Schneider",40,3.5,null,null,3.5,"Installationsschütz iCT 40A 4S 220/240V 50Hz MO"]
["Installationsschütz","INST.SCHÜTZ ICT+ 3PN 4Ö 40A 220-240VAC","A9C22740",2.1,"Schneider",40,3.5,null,null,3.5,"INST.SCHÜTZ ICT+ 3PN 4Ö 40A 220-240VAC"]
["Installationsschütz","INST.SCHÜTZ ICT+ 3PN 40A 4S 220-240VAC","A9C24740",2.1,"Schneider",40,3.5,null,null,3.5,"INST.SCHÜTZ ICT+ 3PN 40A 4S 220-240VAC"]
["Installationsschütz","Installationsschütz iCT 63A 2S 24V 50Hz","A9C20162",1.6,"Schneider",63,7,null,null,7,"Installationsschütz iCT 63A 2S 24V 50Hz"]
["Installationsschütz","Installationsschütz iCT 63A 2S 220/240V 50Hz","A9C20862",1.6,"Schneider",63,7,null,null,7,"Installationsschütz iCT 63A 2S 220/240V 50Hz"]
["Installationsschütz","Installationsschütz iCT 63A 2S 24V 50Hz MO","A9C21162",1.6,"Schneider",63,7,null,null,7,"Installationsschütz iCT 63A 2S 24V 50Hz MO"]
["Installationsschütz","Installationsschütz iCT 63A 2S 220/240V 50Hz MO","A9C21862",1.6,"Schneider",63,7,null,null,7,"Installationsschütz iCT 63A 2S 220/240V 50Hz MO"]
["Installationsschütz","Installationsschütz iCT 63A 3S 220/240V 60Hz","A9C20663",2.1,"Schneider",63,7,null,null,7,"Installationsschütz iCT 63A 3S 220/240V 60Hz"]
["Installationsschütz","Installationsschütz iCT 63A 3S 220/240V 50Hz","A9C20863",2.1,"Schneider",63,7,null,null,7,"Installationsschütz iCT 63A 3S 220/240V 50Hz"]
["Installationsschütz","Installationsschütz iCT 63A 4S 24V 50Hz","A9C20164",2.1,"Schneider",63,7,null,null,7,"Installationsschütz iCT 63A 4S 24V 50Hz"]
["Installationsschütz","Installationsschütz iCT 63A 4Ö 24V 50Hz","A9C20167",2.1,"Schneider",63,7,null,null,7,"Installationsschütz iCT 63A 4Ö 24V 50Hz"]
["Installationsschütz","Installationsschütz iCT 63A 4S 220/240V 50Hz","A9C20864",2.1,"Schneider",63,7,null,null,7,"Installationsschütz iCT 63A 4S 220/240V 50Hz"]
["Installationsschütz","Installationsschütz iCT 63A 4Ö 220/240V 50Hz","A9C20867",2.1,"Schneider",63,7,null,null,7,"Installationsschütz iCT 63A 4Ö 220/240V 50Hz"]
["Installationsschütz","Installationsschütz iCT 63A 4Ö 220/240V 50Hz","A9C20868",2.1,"Schneider",63,7,null,null,7,"Installationsschütz iCT 63A 4Ö 220/240V 50Hz"]
["Installationsschütz","Installationsschütz iCT 63A 3S+1Ö 220/240V 50Hz","A9C20869",2.1,"Schneider",63,7,null,null,7,"Installationsschütz iCT 63A 3S+1Ö 220/240V 50Hz"]
["Installationsschütz","Installationsschütz iCT 63A 4Ö 220/240V 50Hz","A9C20882",2.1,"Schneider",63,7,null,null,7,"Installationsschütz iCT 63A 4Ö 220/240V 50Hz"]
["Installationsschütz","Installationsschütz iCT 63A 4S 24V 50Hz MO","A9C21164",2.1,"Schneider",63,7,null,null,7,"Installationsschütz iCT 63A 4S 24V 50Hz MO"]
["Installationsschütz","Installationsschütz iCT 63A 4S 220/240V 50Hz MO","A9C21864",2.1,"Schneider",63,7,null,null,7,"Installationsschütz iCT 63A 4S 220/240V 50Hz MO"]
["Installationsschütz","INST.SCHÜTZ ICT+ 3PN 4Ö 63A 220-240VAC","A9C22763",2.1,"Schneider",63,7,null,null,7,"INST.SCHÜTZ ICT+ 3PN 4Ö 63A 220-240VAC"]
["Installationsschütz","INST.SCHÜTZ ICT+ 3PN 4S 63A 220-240VAC","A9C24763",2.1,"Schneider",63,7,null,null,7,"INST.SCHÜTZ ICT+ 3PN 4S 63A 220-240VAC"]
["Installationsschütz","Installationsschütz iCT 100A 4S 220/240V 50Hz","A9C20884",4.2,"Schneider",100,9,null,null,9,"Installationsschütz iCT 100A 4S 220/240V 50Hz"]
[null,null,null,null,null,null,null,null,null,0]
["Fernschalter","Fernschalter/Stromstoßschalter ",null,null,null,null,null,null,null,0,"Fernschalter/Stromstoßschalter "]
["Fernschalter","Fernschalter iTL, 2p, 2 S, 16A, Spule 12 VAC 50/60 Hz- 6 VDC","A9C30012",null,"Schneider",16,0.6,{"$f":"G1901*2","v":1.2},null,0.6,"Fernschalter iTL, 2p, 2 S, 16A, Spule 12 VAC 50/60 Hz- 6 VDC"]
["Fernschalter","Fernschalter iTLI, 2p, 1S+1Ö, 16A, Spule 12 VAC 50 /60Hz- 6 VDC","A9C30015",null,"Schneider",16,0.6,0.6,null,0.6,"Fernschalter iTLI, 2p, 1S+1Ö, 16A, Spule 12 VAC 50 /60Hz- 6 VDC"]
["Fernschalter","Fernschalter iTL, 1p, 1S, 16A, Spule 24 VAC,12 VDC  50/60Hz","A9C30111",null,"Schneider",16,0.6,0.6,null,0.6,"Fernschalter iTL, 1p, 1S, 16A, Spule 24 VAC,12 VDC  50/60Hz"]
["Fernschalter","Fernschalter iTL, 2p, 2 S, 16A, Spule 12 VDC, 24 V AC 50/60Hz","A9C30112",null,"Schneider",16,0.6,{"$f":"G1904*2","v":1.2},null,0.6,"Fernschalter iTL, 2p, 2 S, 16A, Spule 12 VDC, 24 V AC 50/60Hz"]
["Fernschalter","Fernschalter iTLI, 2p, 1S+1Ö, 16A, Spule 12 VDC, 2 4 VAC 50/60Hz","A9C30115",null,"Schneider",16,0.6,0.6,null,0.6,"Fernschalter iTLI, 2p, 1S+1Ö, 16A, Spule 12 VDC, 2 4 VAC 50/60Hz"]
["Fernschalter","Fernschalter iTL, 1p, 1S, 16A, Spule 24 VDC, 48 VA C 50/60Hz","A9C30211",null,"Schneider",16,0.6,0.6,null,0.6,"Fernschalter iTL, 1p, 1S, 16A, Spule 24 VDC, 48 VA C 50/60Hz"]
["Fernschalter","Fernschalter iTL, 2p, 2 S, 16A, Spule 24 VDC, 48 V AC 50/60Hz","A9C30212",null,"Schneider",16,0.6,{"$f":"G1907*2","v":1.2},null,{"$f":"G1907+I1907","v":0.6},"Fernschalter iTL, 2p, 2 S, 16A, Spule 24 VDC, 48 V AC 50/60Hz"]
["Fernschalter","Fernschalter iTLI, 2p, 1S+1Ö, 16A, Spule 24 VDC, 4 8 VAC 50/60Hz","A9C30215",null,"Schneider",16,0.6,0.6,null,0.6,"Fernschalter iTLI, 2p, 1S+1Ö, 16A, Spule 24 VDC, 4 8 VAC 50/60Hz"]
["Fernschalter","Fernschalter iTL, 1p, 1S, 16A, Spule 130 VAC 50/60 Hz- 48 VDC","A9C30311",null,"Schneider",16,0.6,0.6,null,0.6,"Fernschalter iTL, 1p, 1S, 16A, Spule 130 VAC 50/60 Hz- 48 VDC"]
["Fernschalter","Fernschalter iTL, 2p, 2 S, 16A, Spule 130 VAC 50/6 0Hz- 48 VDC","A9C30312",null,"Schneider",16,0.6,{"$f":"G1910*2","v":1.2},null,0.6,"Fernschalter iTL, 2p, 2 S, 16A, Spule 130 VAC 50/6 0Hz- 48 VDC"]
["Fernschalter","Fernschalter iTLI, 2p, 1S+1Ö, 16A, Spule 130 VAC 5 0/60Hz- 48 VDC","A9C30315",null,"Schneider",16,0.6,0.6,null,0.6,"Fernschalter iTLI, 2p, 1S+1Ö, 16A, Spule 130 VAC 5 0/60Hz- 48 VDC"]
["Fernschalter","Fernschalter iTL, 1p, 1S, 16A, Spule  230V AC 110V DC, 50/60Hz","A9C30811",null,"Schneider",16,0.6,0.6,null,0.6,"Fernschalter iTL, 1p, 1S, 16A, Spule  230V AC 110V DC, 50/60Hz"]
["Fernschalter","Fernschalter iTL, 2p, 2 S, 16A, Spule  230V AC 110 VDC 50/60Hz","A9C30812",null,"Schneider",16,0.6,{"$f":"G1913*2","v":1.2},null,0.6,"Fernschalter iTL, 2p, 2 S, 16A, Spule  230V AC 110 VDC 50/60Hz"]
["Fernschalter","Fernschalter iTL, 4p, 4 S, 16A, Spule 110 VDC, 230 -240 VAC 50/60Hz","A9C30814",null,"Schneider",16,0.6,{"$f":"3*G1914","v":1.7999999999999998},null,0.6,"Fernschalter iTL, 4p, 4 S, 16A, Spule 110 VDC, 230 -240 VAC 50/60Hz"]
["Fernschalter","Fernschalter iTLI, 2P, 1S+1Ö, 16A, Spule 110VDC, 230-240VAC 50/60Hz","A9C30815",null,"Schneider",16,0.6,{"$f":"3*G1915","v":1.7999999999999998},null,{"$f":"G1915+I1915","v":0.6},"Fernschalter iTLI, 2P, 1S+1Ö, 16A, Spule 110VDC, 230-240VAC 50/60Hz"]
["Fernschalter","Fernschalter iTLs, 1p, 1S, 16A, Spule 12 VDC, 24 V AC 50/60Hz","A9C32111",null,"Schneider",16,0.6,0.6,null,0.6,"Fernschalter iTLs, 1p, 1S, 16A, Spule 12 VDC, 24 V AC 50/60Hz"]
["Fernschalter","Erweiterung iETL iTL 16, 2p, 1W+1S, 16A, Spule 12V DC, 24VAC 50/60Hz","A9C32116",null,"Schneider",16,0.6,{"$f":"G1917*2","v":1.2},null,0.6,"Erweiterung iETL iTL 16, 2p, 1W+1S, 16A, Spule 12V DC, 24VAC 50/60Hz"]
["Fernschalter","Fernschalter iTLs, 1p, 1S, 16A, Spule 24 VDC, 48 V AC 50/60Hz","A9C32211",null,"Schneider",16,0.6,0.6,null,0.6,"Fernschalter iTLs, 1p, 1S, 16A, Spule 24 VDC, 48 V AC 50/60Hz"]
["Fernschalter","Erweiterung iETL iTL 16, 2p, 1W+1S, 16A, Spule 24V DC, 48VAC 50/60Hz","A9C32216",null,"Schneider",16,0.6,{"$f":"G1919*2","v":1.2},null,0.6,"Erweiterung iETL iTL 16, 2p, 1W+1S, 16A, Spule 24V DC, 48VAC 50/60Hz"]
["Fernschalter","Erweiterung iETL iTL 16, 2p, 1W+1S, 16A, Spule 130 VAC 50/60Hz, 48VDC","A9C32316",null,"Schneider",16,0.6,{"$f":"G1920*2","v":1.2},null,0.6,"Erweiterung iETL iTL 16, 2p, 1W+1S, 16A, Spule 130 VAC 50/60Hz, 48VDC"]
["Fernschalter","Fernschalter iTLs, 1p, 1S, 16A, Spule 110 VDC, 230 -240 VAC 50/60Hz","A9C32811",null,"Schneider",16,0.6,0.6,null,0.6,"Fernschalter iTLs, 1p, 1S, 16A, Spule 110 VDC, 230 -240 VAC 50/60Hz"]
["Fernschalter","Erweiterung iETL iTL 16- 2p, 1W+1S -16A, Spule 110 VDC, 230-240V AC 50/60Hz","A9C32816",null,"Schneider",16,0.6,{"$f":"G1922*2","v":1.2},null,0.6,"Erweiterung iETL iTL 16- 2p, 1W+1S -16A, Spule 110 VDC, 230-240V AC 50/60Hz"]
["Fernschalter","Fernschalter iTLc, 1p, 1S, 16A, Spule 24 VAC 50/60 Hz-","A9C33111",null,"Schneider",16,0.6,0.6,null,0.6,"Fernschalter iTLc, 1p, 1S, 16A, Spule 24 VAC 50/60 Hz-"]
["Fernschalter","Fernschalter iTLc, 1p, 1S, 16A, Spule 48 VAC 50/60 Hz-","A9C33211",null,"Schneider",16,0.6,0.6,null,0.6,"Fernschalter iTLc, 1p, 1S, 16A, Spule 48 VAC 50/60 Hz-"]
["Fernschalter","Fernschalter iTLc, 1p, 1S, 16A, Spule 230-240 VAC  50/60Hz-","A9C33811",null,"Schneider",16,0.6,0.6,null,0.6,"Fernschalter iTLc, 1p, 1S, 16A, Spule 230-240 VAC  50/60Hz-"]
["Fernschalter","Fernschalter iTLm, 1p, 1S, 16A, Spule 230-240 VAC  50/60Hz","A9C34811",null,"Schneider",16,0.6,0.6,null,0.6,"Fernschalter iTLm, 1p, 1S, 16A, Spule 230-240 VAC  50/60Hz"]
["Fernschalter","Fernschalter iTL, 1p, 1S, 32A, Spule 110 VDC, 230- 240 VAC 50/60Hz","A9C30831",null,"Schneider",32,1.5,1.5,null,1.5,"Fernschalter iTL, 1p, 1S, 32A, Spule 110 VDC, 230- 240 VAC 50/60Hz"]
["Fernschalter","Erweiterung ETL iTL 32, 1p -1S, 32A, Spule 110 VDC , 230-240VAC 50/60Hz","A9C32836",null,"Schneider",32,1.5,1.5,null,1.5,"Erweiterung ETL iTL 32, 1p -1S, 32A, Spule 110 VDC , 230-240VAC 50/60Hz"]
["Fernschalter","Reflex iC60N Ti24 16A 2P B, Fernschaltbarer Leitungsschutzschalter","A9C61216",null,"Schneider","16",2.4,null,null,2.4,"Reflex iC60N Ti24 16A 2P B, Fernschaltbarer Leitungsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 10A 2p B, Fernschaltbarer Leitun gsschutzschalter","A9C61210",null,"Schneider",10,2.2999999999999998,null,null,{"$f":"G1930+I1930","v":2.2999999999999998},"Reflex iC60N Ti24 10A 2p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 25A 2p B, Fernschaltbarer Leitun gsschutzschalter","A9C61225",null,"Schneider",25,3,null,null,3,"Reflex iC60N Ti24 25A 2p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 40A 2p B, Fernschaltbarer Leitun gsschutzschalter","A9C61240",null,"Schneider",40,3.6,null,null,3.6,"Reflex iC60N Ti24 40A 2p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 63A 2p B, Fernschaltbarer Leitun gsschutzschalter","A9C61263",null,"Schneider",63,5.6,null,null,5.6,"Reflex iC60N Ti24 63A 2p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 10A 3p B, Fernschaltbarer Leitun gsschutzschalter","A9C61310",null,"Schneider",10,2.2999999999999998,null,null,{"$f":"G1934+I1934","v":2.2999999999999998},"Reflex iC60N Ti24 10A 3p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 16A 3p B, Fernschaltbarer Leitun gsschutzschalter","A9C61316",null,"Schneider",16,2.4,null,null,2.4,"Reflex iC60N Ti24 16A 3p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 25A 3p B, Fernschaltbarer Leitun gsschutzschalter","A9C61325",null,"Schneider",25,3,null,null,3,"Reflex iC60N Ti24 25A 3p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 40A 3p B, Fernschaltbarer Leitun gsschutzschalter","A9C61340",null,"Schneider",40,3.6,null,null,3.6,"Reflex iC60N Ti24 40A 3p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 63A 3p B, Fernschaltbarer Leitun gsschutzschalter","A9C61363",null,"Schneider",63,5.6,null,null,5.6,"Reflex iC60N Ti24 63A 3p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 10A 4p B, Fernschaltbarer Leitun gsschutzschalter","A9C61410",null,"Schneider",10,2.2999999999999998,null,null,2.2999999999999998,"Reflex iC60N Ti24 10A 4p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 16A 4p B, Fernschaltbarer Leitun gsschutzschalter","A9C61416",null,"Schneider",16,2.4,null,null,2.4,"Reflex iC60N Ti24 16A 4p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 25A 4p B, Fernschaltbarer Leitun gsschutzschalter","A9C61425",null,"Schneider",25,3,null,null,3,"Reflex iC60N Ti24 25A 4p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 40A 4p B, Fernschaltbarer Leitun gsschutzschalter","A9C61440",null,"Schneider",40,3.6,null,null,3.6,"Reflex iC60N Ti24 40A 4p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 63A 4p B, Fernschaltbarer Leitun gsschutzschalter","A9C61463",null,"Schneider",63,5.6,null,null,5.6,"Reflex iC60N Ti24 63A 4p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 10A 2p C, Fernschaltbarer Leitun gsschutzschalter","A9C62210",null,"Schneider",10,2.2999999999999998,null,null,2.2999999999999998,"Reflex iC60N Ti24 10A 2p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 16A 2p C, Fernschaltbarer Leitun gsschutzschalter","A9C62216",null,"Schneider",16,2.4,null,null,2.4,"Reflex iC60N Ti24 16A 2p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 25A 2p C, Fernschaltbarer Leitun gsschutzschalter","A9C62225",null,"Schneider",25,3,null,null,3,"Reflex iC60N Ti24 25A 2p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 40A 2p C, Fernschaltbarer Leitun gsschutzschalter","A9C62240",null,"Schneider",40,3.6,null,null,3.6,"Reflex iC60N Ti24 40A 2p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 63A 2p C, Fernschaltbarer Leitun gsschutzschalter","A9C62263",null,"Schneider",63,5.6,null,null,5.6,"Reflex iC60N Ti24 63A 2p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 10A 3p C, Fernschaltbarer Leitun gsschutzschalter","A9C62310",null,"Schneider",10,2.2999999999999998,null,null,2.2999999999999998,"Reflex iC60N Ti24 10A 3p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 16A 3p C, Fernschaltbarer Leitun gsschutzschalter","A9C62316",null,"Schneider",16,2.4,null,null,2.4,"Reflex iC60N Ti24 16A 3p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 25A 3p C, Fernschaltbarer Leitun gsschutzschalter","A9C62325",null,"Schneider",25,3,null,null,3,"Reflex iC60N Ti24 25A 3p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 40A 3p C, Fernschaltbarer Leitun gsschutzschalter","A9C62340",null,"Schneider",40,3.6,null,null,3.6,"Reflex iC60N Ti24 40A 3p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 63A 3p C, Fernschaltbarer Leitun gsschutzschalter","A9C62363",null,"Schneider",63,5.6,null,null,5.6,"Reflex iC60N Ti24 63A 3p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 10A 4p C, Fernschaltbarer Leitun gsschutzschalter","A9C62410",null,"Schneider",10,2.2999999999999998,null,null,2.2999999999999998,"Reflex iC60N Ti24 10A 4p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 16A 4p C, Fernschaltbarer Leitun gsschutzschalter","A9C62416",null,"Schneider",16,2.4,null,null,2.4,"Reflex iC60N Ti24 16A 4p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 25A 4p C, Fernschaltbarer Leitun gsschutzschalter","A9C62425",null,"Schneider",25,3,null,null,3,"Reflex iC60N Ti24 25A 4p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 40A 4p C, Fernschaltbarer Leitun gsschutzschalter","A9C62440",null,"Schneider",40,3.6,null,null,3.6,"Reflex iC60N Ti24 40A 4p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 63A 4p C, Fernschaltbarer Leitun gsschutzschalter","A9C62463",null,"Schneider",63,5.6,null,null,5.6,"Reflex iC60N Ti24 63A 4p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 10A 2p D, Fernschaltbarer Leitun gsschutzschalter","A9C63210",null,"Schneider",10,2.2999999999999998,null,null,2.2999999999999998,"Reflex iC60N Ti24 10A 2p D, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 16A 2p D, Fernschaltbarer Leitun gsschutzschalter","A9C63216",null,"Schneider",16,2.4,null,null,2.4,"Reflex iC60N Ti24 16A 2p D, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 25A 2p D, Fernschaltbarer Leitun gsschutzschalter","A9C63225",null,"Schneider",25,3,null,null,3,"Reflex iC60N Ti24 25A 2p D, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 10A 3p D, Fernschaltbarer Leitun gsschutzschalter","A9C63310",null,"Schneider",10,2.2999999999999998,null,null,2.2999999999999998,"Reflex iC60N Ti24 10A 3p D, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 16A 3p D, Fernschaltbarer Leitun gsschutzschalter","A9C63316",null,"Schneider",16,2.4,null,null,2.4,"Reflex iC60N Ti24 16A 3p D, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 25A 3p D, Fernschaltbarer Leitun gsschutzschalter","A9C63325",null,"Schneider",25,3,null,null,3,"Reflex iC60N Ti24 25A 3p D, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 10A 4p D, Fernschaltbarer Leitun gsschutzschalter","A9C63410",null,"Schneider",10,2.2999999999999998,null,null,2.2999999999999998,"Reflex iC60N Ti24 10A 4p D, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 16A 4p D, Fernschaltbarer Leitun gsschutzschalter","A9C63416",null,"Schneider",16,2.4,null,null,2.4,"Reflex iC60N Ti24 16A 4p D, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60N Ti24 25A 4p D, Fernschaltbarer Leitun gsschutzschalter","A9C63425",null,"Schneider",25,3,null,null,3,"Reflex iC60N Ti24 25A 4p D, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 10A 2p B, Fernschaltbarer Leitun gsschutzschalter","A9C64210",null,"Schneider",10,2.2999999999999998,null,null,2.2999999999999998,"Reflex iC60H Ti24 10A 2p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 16A 2p B, Fernschaltbarer Leitun gsschutzschalter","A9C64216",null,"Schneider",16,2.4,null,null,2.4,"Reflex iC60H Ti24 16A 2p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 25A 2p B, Fernschaltbarer Leitun gsschutzschalter","A9C64225",null,"Schneider",25,3,null,null,3,"Reflex iC60H Ti24 25A 2p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 40A 2p B, Fernschaltbarer Leitun gsschutzschalter","A9C64240",null,"Schneider",40,3.6,null,null,3.6,"Reflex iC60H Ti24 40A 2p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 10A 3p B, Fernschaltbarer Leitun gsschutzschalter","A9C64310",null,"Schneider",10,2.2999999999999998,null,null,2.2999999999999998,"Reflex iC60H Ti24 10A 3p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 16A 3p B, Fernschaltbarer Leitun gsschutzschalter","A9C64316",null,"Schneider",16,2.4,null,null,2.4,"Reflex iC60H Ti24 16A 3p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 25A 3p B, Fernschaltbarer Leitun gsschutzschalter","A9C64325",null,"Schneider",25,3,null,null,3,"Reflex iC60H Ti24 25A 3p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 40A 3p B, Fernschaltbarer Leitun gsschutzschalter","A9C64340",null,"Schneider",40,3.6,null,null,3.6,"Reflex iC60H Ti24 40A 3p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 10A 4p B, Fernschaltbarer Leitun gsschutzschalter","A9C64410",null,"Schneider",10,2.2999999999999998,null,null,2.2999999999999998,"Reflex iC60H Ti24 10A 4p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 16A 4p B, Fernschaltbarer Leitun gsschutzschalter","A9C64416",null,"Schneider",16,2.4,null,null,2.4,"Reflex iC60H Ti24 16A 4p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 25A 4p B, Fernschaltbarer Leitun gsschutzschalter","A9C64425",null,"Schneider",25,3,null,null,3,"Reflex iC60H Ti24 25A 4p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 40A 4p B, Fernschaltbarer Leitun gsschutzschalter","A9C64440",null,"Schneider",40,3.6,null,null,3.6,"Reflex iC60H Ti24 40A 4p B, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 10A 2p C, Fernschaltbarer Leitun gsschutzschalter","A9C65210",null,"Schneider",10,2.2999999999999998,null,null,2.2999999999999998,"Reflex iC60H Ti24 10A 2p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 16A 2p C, Fernschaltbarer Leitun gsschutzschalter","A9C65216",null,"Schneider",16,2.4,null,null,2.4,"Reflex iC60H Ti24 16A 2p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 25A 2p C, Fernschaltbarer Leitun gsschutzschalter","A9C65225",null,"Schneider",25,3,null,null,3,"Reflex iC60H Ti24 25A 2p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 40A 2p C, Fernschaltbarer Leitun gsschutzschalter","A9C65240",null,"Schneider",40,3.6,null,null,3.6,"Reflex iC60H Ti24 40A 2p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 10A 3p C, Fernschaltbarer Leitun gsschutzschalter","A9C65310",null,"Schneider",10,2.2999999999999998,null,null,2.2999999999999998,"Reflex iC60H Ti24 10A 3p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 16A 3p C, Fernschaltbarer Leitun gsschutzschalter","A9C65316",null,"Schneider",16,2.4,null,null,2.4,"Reflex iC60H Ti24 16A 3p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 25A 3p C, Fernschaltbarer Leitun gsschutzschalter","A9C65325",null,"Schneider",25,3,null,null,3,"Reflex iC60H Ti24 25A 3p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 40A 3p C, Fernschaltbarer Leitun gsschutzschalter","A9C65340",null,"Schneider",40,3.6,null,null,3.6,"Reflex iC60H Ti24 40A 3p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 10A 4p C, Fernschaltbarer Leitun gsschutzschalter","A9C65410",null,"Schneider",10,2.2999999999999998,null,null,2.2999999999999998,"Reflex iC60H Ti24 10A 4p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 16A 4p C, Fernschaltbarer Leitun gsschutzschalter","A9C65416",null,"Schneider",16,2.4,null,null,2.4,"Reflex iC60H Ti24 16A 4p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 25A 4p C, Fernschaltbarer Leitun gsschutzschalter","A9C65425",null,"Schneider",25,3,null,null,3,"Reflex iC60H Ti24 25A 4p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 40A 4p C, Fernschaltbarer Leitun gsschutzschalter","A9C65440",null,"Schneider",40,3.6,null,null,3.6,"Reflex iC60H Ti24 40A 4p C, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 10A 2p D, Fernschaltbarer Leitun gsschutzschalter","A9C66210",null,"Schneider",10,2.2999999999999998,null,null,2.2999999999999998,"Reflex iC60H Ti24 10A 2p D, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 16A 2p D, Fernschaltbarer Leitun gsschutzschalter","A9C66216",null,"Schneider",16,2.4,null,null,2.4,"Reflex iC60H Ti24 16A 2p D, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 25A 2p D, Fernschaltbarer Leitun gsschutzschalter","A9C66225",null,"Schneider",25,3,null,null,3,"Reflex iC60H Ti24 25A 2p D, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 10A 3p D, Fernschaltbarer Leitun gsschutzschalter","A9C66310",null,"Schneider",10,2.2999999999999998,null,null,2.2999999999999998,"Reflex iC60H Ti24 10A 3p D, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 16A 3p D, Fernschaltbarer Leitun gsschutzschalter","A9C66316",null,"Schneider",16,2.4,null,null,2.4,"Reflex iC60H Ti24 16A 3p D, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 25A 3p D, Fernschaltbarer Leitun gsschutzschalter","A9C66325",null,"Schneider",25,3,null,null,3,"Reflex iC60H Ti24 25A 3p D, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 10A 4p D, Fernschaltbarer Leitun gsschutzschalter","A9C66410",null,"Schneider",10,2.2999999999999998,null,null,{"$f":"G1998+I1998","v":2.2999999999999998},"Reflex iC60H Ti24 10A 4p D, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 16A 4p D, Fernschaltbarer Leitun gsschutzschalter","A9C66416",null,"Schneider",16,2.4,null,null,2.4,"Reflex iC60H Ti24 16A 4p D, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Reflex iC60H Ti24 25A 4p D, Fernschaltbarer Leitun gsschutzschalter","A9C66425",null,"Schneider",25,3,null,null,3,"Reflex iC60H Ti24 25A 4p D, Fernschaltbarer Leitun gsschutzschalter"]
["Fernschalter","Zentral Ein-/Ausschalten mehrerer Gruppen von Fern schaltern iATLc+c, 24-240V AC","A9C15410",null,"Schneider","-",0.15,null,null,0.15,"Zentral Ein-/Ausschalten mehrerer Gruppen von Fern schaltern iATLc+c, 24-240V AC"]
["Fernschalter","Hilfsmodul iATL24 für Fernschalten iTL mit Ti24-SP S-Schnittstelle, 24V DC","A9C15424",null,"Schneider",0.1,1,null,null,1,"Hilfsmodul iATL24 für Fernschalten iTL mit Ti24-SP S-Schnittstelle, 24V DC"]
["Fernschalter","Hilfsmodul iACT24 für Fernschalten iCT mit Ti24-SP S-Schnittstelle, 24V DC","A9C15924",null,"Schneider",0.1,1,null,null,1,"Hilfsmodul iACT24 für Fernschalten iCT mit Ti24-SP S-Schnittstelle, 24V DC"]
[null,null,null,null,null,null,null,null,null,0]
["Treppenlichtautomat","Treppenlichtautomat",null,null,null,null,null,null,null,0,"Treppenlichtautomat"]
["Treppenlichtautomat","Elektromechanischer Treppenlichtzeitschalter MIN, 1 bis 7 Minuten",15363,null,"Schneider",16,1,1,null,1,"Elektromechanischer Treppenlichtzeitschalter MIN, 1 bis 7 Minuten"]
["Treppenlichtautomat","Elektronischer Treppenlichtzeitschalter MINs, 0,5, 20min.","CCT15232",null,"Schneider",16,6,6,null,6,"Elektronischer Treppenlichtzeitschalter MINs, 0,5, 20min."]
["Treppenlichtautomat","Elektronischer Treppenlichtzeitschalter MINs, 0,5, 20min. , Vorwarnfunktion","CCT15233",null,"Schneider",16,6,6,null,6,"Elektronischer Treppenlichtzeitschalter MINs, 0,5, 20min. , Vorwarnfunktion"]
["Treppenlichtautomat","Elektr. Treppenlichtzeits. MINs-0,5, 20min., Vorwarnfunkt., Fernschaltfunkt.","CCT15234",null,"Schneider",16,6,6,null,6,"Elektr. Treppenlichtzeits. MINs-0,5, 20min., Vorwarnfunkt., Fernschaltfunkt."]
[null,null,null,null,null,null,null,null,null,0]
["Zeitschaltuhr","Zeitschaltuhr",null,null,null,null,null,null,null,0,"Zeitschaltuhr"]
["Zeitschaltuhr","Mechanische Zeitschaltuhr, IH 60mn 1c SRM, 60min, ohne Speicher","CCT15338",null,"Schneider",16,0.9,0.9,null,0.9,"Mechanische Zeitschaltuhr, IH 60mn 1c SRM, 60min, ohne Speicher"]
["Zeitschaltuhr","DIGITALE ZEITSCHALTUHR IHP+, 1 KANAL","CCT15551",null,"Schneider",16,0.5,0.5,null,0.5,"DIGITALE ZEITSCHALTUHR IHP+, 1 KANAL"]
["Zeitschaltuhr","DIGITALE ZEITSCHALTUHR IHP+, 2 KANAL","CCT15553",null,"Schneider",16,0.5,0.5,null,0.5,"DIGITALE ZEITSCHALTUHR IHP+, 2 KANAL"]
["Zeitschaltuhr","Mechanische Zeitschaltuhr, IH 24h 1c SRM, 24 Std.,  ohne Speicher","CCT16364",null,"Schneider",16,0.5,0.5,null,0.5,"Mechanische Zeitschaltuhr, IH 24h 1c SRM, 24 Std.,  ohne Speicher"]
["Zeitschaltuhr","Digitale Zeitschaltuhr, IHP 1c, 24 Std.+7 Tage, 1, Kanal","CCT15720",null,"Schneider",16,4,4,null,4,"Digitale Zeitschaltuhr, IHP 1c, 24 Std.+7 Tage, 1, Kanal"]
["Zeitschaltuhr","Acti 9 Digitale Zeitschaltuhr IHP, 1C (24h / 7d) Programmierbare, digitale Zeitschalter","CCT15441",null,"Schneider",16,0.5,null,null,{"$f":"G2017+I2017","v":0.5},"Acti 9 Digitale Zeitschaltuhr IHP, 1C (24h / 7d) Programmierbare, digitale Zeitschalter"]
["Zeitschaltuhr","Digitale Zeitschaltuhr IHP 2Kanal,  2Wechsler","CCT15443",null,"Schneider",16,0.5,null,null,0.5,"Digitale Zeitschaltuhr IHP 2Kanal,  2Wechsler"]
["Zeitschaltuhr","Digitale Zeitschaltuhr 1 Kanal ,IHP DCF, Bluetooth","CCT15858",null,"Schneider",16,0.8,null,null,0.8,"Digitale Zeitschaltuhr 1 Kanal ,IHP DCF, Bluetooth"]
["Zeitschaltuhr","Acti 9, ITA, 1C Jahreszeitschalter,  24 Stunden+7 Tage+Jahr","CCT15910",null,"Schneider",16,0.8,null,null,0.8,"Acti 9, ITA, 1C Jahreszeitschalter,  24 Stunden+7 Tage+Jahr"]
["Zeitschaltuhr","Acti 9, IHP, 4C Jahreszeitschalter,   24 Stunden+7 Tage+Jahr","CCT15940",null,"Schneider",16,0.8,null,null,0.8,"Acti 9, IHP, 4C Jahreszeitschalter,   24 Stunden+7 Tage+Jahr"]
["Zeitschaltuhr","Acti 9, IHP+1C 18mm Digitale Zeitschaltuhr  mit Wochenprogrammierung","CCT15838",null,"Schneider",16,0.5,null,null,0.5,"Acti 9, IHP+1C 18mm Digitale Zeitschaltuhr  mit Wochenprogrammierung"]
["Zeitschaltuhr","Digitale Zeitschaltuhr, IHP 1c , 18mm, 24 Std.+7 T age, 1 Kanal","CCT15854",null,"Schneider",16,0.5,null,null,0.5,"Digitale Zeitschaltuhr, IHP 1c , 18mm, 24 Std.+7 T age, 1 Kanal"]
["Zeitschaltuhr","Mechanische Zeitschaltuhr, IH 24h 1c ARM, 24 h, 20 0 Std. Speicher","CCT15365",null,"Schneider",16,0.5,null,null,0.5,"Mechanische Zeitschaltuhr, IH 24h 1c ARM, 24 h, 20 0 Std. Speicher"]
["Zeitschaltuhr","Mechanische Zeitschaltuhr, IH 7j 1c ARM, 7 Tage, 2 00 Std. Speicher","CCT15367",null,"Schneider",16,0.5,null,null,0.5,"Mechanische Zeitschaltuhr, IH 7j 1c ARM, 7 Tage, 2 00 Std. Speicher"]
[null,null,null,null,null,null,null,null,null,0]
["Zeitrelais","Zeitrelais",null,null,null,null,null,null,null,0,"Zeitrelais"]
["Zeitrelais","Zeitrelais iRTB, Zeitverzögerung, 1W, 24-240VAC, 24VDC","A9E16066",null,"Schneider",null,2.5,2.5,null,2.5,"Zeitrelais iRTB, Zeitverzögerung, 1W, 24-240VAC, 24VDC"]
["Zeitrelais","Zeitrelais verzögert, iRTA, 1W, 24-240VAC /  24VDC  Ansprechverzögerung","A9E16065",null,"Schneider",null,2.5,2.5,null,2.5,"Zeitrelais verzögert, iRTA, 1W, 24-240VAC /  24VDC  Ansprechverzögerung"]
["Zeitrelais","Zeitverzögertes Rückfallrelais iRTC, 1W, 0,1 sec-100 Std., 24-240VAC, 24VDC","A9E16067",null,"Schneider",null,2.5,2.5,null,2.5,"Zeitverzögertes Rückfallrelais iRTC, 1W, 0,1 sec-100 Std., 24-240VAC, 24VDC"]
["Zeitrelais","Multifunktionsrelais iRTMF, 1 W, 12-240V AC/DC","A9E16070",null,"Schneider",null,2.5,2.5,null,2.5,"Multifunktionsrelais iRTMF, 1 W, 12-240V AC/DC"]
[]
["Zähler","Zähler"]
["Zähler","Energiezähler iEM2435, 1-phasig 230V, 100A, MID M-Bus, 2 S0-Impuls, Genauigkeitsklasse 1","A9MEM2435",null,"Schneider",100,1,null,null,{"$f":"G2034+I2034","v":1},"Energiezähler iEM2435, 1-phasig 230V, 100A, MID M-Bus, 2 S0-Impuls, Genauigkeitsklasse 1"]
["Zähler","Energiezähler, 3-phasig, 63A, mit Teilzähler","A9MEM3100",null,"Schneider",63,1,null,null,1,"Energiezähler, 3-phasig, 63A, mit Teilzähler"]
["Zähler","Energiezähler, 3-phasig, 63A, mit Teilzähler S0-Impuls, MID konform","A9MEM3110",null,"Schneider",63,1,null,null,1,"Energiezähler, 3-phasig, 63A, mit Teilzähler S0-Impuls, MID konform"]
["Zähler","Energiezähler,3 - phasig, 63A, M-Bus, MID konform","A9MEM3135",null,"Schneider",63,1,null,null,1,"Energiezähler,3 - phasig, 63A, M-Bus, MID konform"]
["Zähler","Energiezähler, 3-phasig, 63A erweiterte Messfunktion, Modbus","A9MEM3150",null,"Schneider",63,1,null,null,1,"Energiezähler, 3-phasig, 63A erweiterte Messfunktion, Modbus"]
["Zähler","Energiezähler,3 - phasig, 63A, Modbus, MID konform","A9MEM3155",null,"Schneider",63,1,null,null,1,"Energiezähler,3 - phasig, 63A, Modbus, MID konform"]
["Zähler","PM3255-Messgerät, 2 digitale E 2 digitale A, RS485","METSEPM3255",null,"Schneider",5,5,null,null,5,"PM3255-Messgerät, 2 digitale E 2 digitale A, RS485"]
["Zähler","Universalmessgerät PM5100, Fronteinbau konfig. Transistor Ausgang, bis zur 15. H","METSEPM5100",null,"Schneider",5,11,null,null,11,"Universalmessgerät PM5100, Fronteinbau konfig. Transistor Ausgang, bis zur 15. H"]
["Zähler","PM5110-Messgerät mit Modbus, bis 15. H, 1DA 33Alarme, flächenbündige Montage","METSEPM5110",null,"Schneider",5,11,null,null,11,"PM5110-Messgerät mit Modbus, bis 15. H, 1DA 33Alarme, flächenbündige Montage"]
["Zähler","PM5320-Messgerät mit Ethernet, bis 31. H, 256K 2DE/2DA 35Alarme","METSEPM5320",null,"Schneider",5,11,null,null,11,"PM5320-Messgerät mit Ethernet, bis 31. H, 256K 2DE/2DA 35Alarme"]
["Zähler","Universalmessgerät PM5560, Fronteinbau,Modbus RTU, Ethernet, 4 konfig. dig. Eingänge, 2 Transistor Au","METSEPM5560",null,"Schneider",5,11,null,null,11,"Universalmessgerät PM5560, Fronteinbau,Modbus RTU, Ethernet, 4 konfig. dig. Eingänge, 2 Transistor Au"]
["Zähler","Netzanalysator PM8240,Fronteinbau","METSEPM8240",null,"Schneider",10,16,null,null,16,"Netzanalysator PM8240,Fronteinbau"]
["Zähler","Energiezähler, 1-phasig, 40A, MID konform Analog","A9MEM2000",null,"Schneider",40,10,null,null,10,"Energiezähler, 1-phasig, 40A, MID konform Analog"]
["Zähler","Energiezähler, 1-phasig, 40A, S0-Impuls, MID konfo rm","A9MEM2010",null,"Schneider",40,10,null,null,10,"Energiezähler, 1-phasig, 40A, S0-Impuls, MID konfo rm"]
["Zähler","Kompakter Energiezähler PowerTag Flex zur einphasige Direktmessung bis 63A","A9MEM1560",null,"Schneider",63,0.01,null,null,0.01,"Kompakter Energiezähler PowerTag Flex zur einphasige Direktmessung bis 63A"]
[]
["Fehlerlichtbogen-Schutzschalter","Fehlerlichtbogen-Schutzschalter"]
["Fehlerlichtbogen-Schutzschalter","ACTI9 ICV40N 1P+N 10A B 30MA AFDD+FI/LS","A9TDE3610",null,"Schneider",10,2.9,null,null,2.9,"ACTI9 ICV40N 1P+N 10A B 30MA AFDD+FI/LS"]
["Fehlerlichtbogen-Schutzschalter","ACTI9 ICV40N 1P+N 16A B 30MA AFDD+FI/LS","A9TDE3616",null,"Schneider",16,4.3,null,null,4.3,"ACTI9 ICV40N 1P+N 16A B 30MA AFDD+FI/LS"]
["Fehlerlichtbogen-Schutzschalter","ACTI9 IC40N ARC 1P+N 10A B AFDD + LS-SCH","A9TPD4610",null,"Schneider",10,2.9,null,null,2.9,"ACTI9 IC40N ARC 1P+N 10A B AFDD + LS-SCH"]
["Fehlerlichtbogen-Schutzschalter","ACTI9 IC40N ARC 1P+N 13A B AFDD + LS-SCH","A9TPD4613",null,"Schneider",13,3.3,null,null,3.3,"ACTI9 IC40N ARC 1P+N 13A B AFDD + LS-SCH"]
["Fehlerlichtbogen-Schutzschalter","ACTI9 IC40N ARC 1P+N 16A B AFDD + LS-SCH","A9TPD4616",null,"Schneider",16,3.4,null,null,3.4,"ACTI9 IC40N ARC 1P+N 16A B AFDD + LS-SCH"]
[]
["FI-Block","FI-Block"]
["FI-Block","FI-Block Vigi C120, 2p, 300mA, Typ A selektiv, SI","A9N18556",null,"Schneider",125,3.6,null,null,{"$f":"G2058+I2058","v":3.6},"FI-Block Vigi C120, 2p, 300mA, Typ A selektiv, SI"]
["FI-Block","FI-Block Vigi C120, 2p, 1000mA, Typ A selektiv, SI","A9N18557",null,"Schneider",125,3.6,null,null,3.6,"FI-Block Vigi C120, 2p, 1000mA, Typ A selektiv, SI"]
["FI-Block","FI-Block Vigi C120, 3p, 300mA, Typ A selektiv, SI","A9N18558",null,"Schneider",125,3.6,null,null,3.6,"FI-Block Vigi C120, 3p, 300mA, Typ A selektiv, SI"]
["FI-Block","FI-Block Vigi C120, 3p, 1000mA, Typ A selektiv, SI","A9N18559",null,"Schneider",125,3.6,null,null,3.6,"FI-Block Vigi C120, 3p, 1000mA, Typ A selektiv, SI"]
["FI-Block","FI-Block Vigi C120, 4p, 300mA, Typ A selektiv, SI","A9N18560",null,"Schneider",125,3.6,null,null,3.6,"FI-Block Vigi C120, 4p, 300mA, Typ A selektiv, SI"]
["FI-Block","FI-Block Vigi C120, 4p, 1000mA, Typ A selektiv, SI","A9N18561",null,"Schneider",125,3.6,null,null,3.6,"FI-Block Vigi C120, 4p, 1000mA, Typ A selektiv, SI"]
["FI-Block","FI-Block Vigi C120, 2p, 30mA, Typ A","A9N18572",null,"Schneider",125,3.6,null,null,3.6,"FI-Block Vigi C120, 2p, 30mA, Typ A"]
["FI-Block","FI-Block Vigi C120, 2p, 300mA, Typ A","A9N18573",null,"Schneider",125,3.6,null,null,3.6,"FI-Block Vigi C120, 2p, 300mA, Typ A"]
["FI-Block","FI-Block Vigi C120, 2p, 500mA, Typ A","A9N18574",null,"Schneider",125,3.6,null,null,3.6,"FI-Block Vigi C120, 2p, 500mA, Typ A"]
["FI-Block","FI-Block Vigi C120, 3p, 30mA, Typ A","A9N18575",null,"Schneider",125,3.6,null,null,3.6,"FI-Block Vigi C120, 3p, 30mA, Typ A"]
["FI-Block","FI-Block Vigi C120, 3p, 300mA, Typ A","A9N18576",null,"Schneider",125,3.6,null,null,3.6,"FI-Block Vigi C120, 3p, 300mA, Typ A"]
["FI-Block","FI-Block Vigi C120, 3p, 500mA, Typ A","A9N18577",null,"Schneider",125,3.6,null,null,3.6,"FI-Block Vigi C120, 3p, 500mA, Typ A"]
["FI-Block","FI-Block Vigi C120, 4p, 30mA, Typ A","A9N18578",null,"Schneider",125,3.6,null,null,3.6,"FI-Block Vigi C120, 4p, 30mA, Typ A"]
["FI-Block","FI-Block Vigi C120, 4p, 300mA, Typ A","A9N18579",null,"Schneider",125,3.6,null,null,3.6,"FI-Block Vigi C120, 4p, 300mA, Typ A"]
["FI-Block","FI-Block Vigi C120, 4p, 500mA, Typ A","A9N18580",null,"Schneider",125,3.6,null,null,3.6,"FI-Block Vigi C120, 4p, 500mA, Typ A"]
["FI-Block","FI-Block Vigi C120, 4p, 300mA, Typ A selektiv","A9N18587",null,"Schneider",125,3.6,null,null,3.6,"FI-Block Vigi C120, 4p, 300mA, Typ A selektiv"]
["FI-Block","FI-Block Vigi C120, 4p, 500mA, Typ A selektiv","A9N18588",null,"Schneider",125,3.6,null,null,3.6,"FI-Block Vigi C120, 4p, 500mA, Typ A selektiv"]
["FI-Block","FI-Block Vigi C120, 4p, 1000mA, Typ A selektiv","A9N18589",null,"Schneider",125,3.6,null,null,3.6,"FI-Block Vigi C120, 4p, 1000mA, Typ A selektiv"]
["FI-Block","FI-Block Vigi C120, 2p, 30mA, Typ A si","A9N18591",null,"Schneider",125,3.6,null,null,3.6,"FI-Block Vigi C120, 2p, 30mA, Typ A si"]
["FI-Block","FI-Block Vigi C120, 2p, 300mA, Typ A si","A9N18592",null,"Schneider",125,3.6,null,null,3.6,"FI-Block Vigi C120, 2p, 300mA, Typ A si"]
["FI-Block","FI-Block Vigi C120, 3p, 30mA, Typ A si","A9N18594",null,"Schneider",125,3.6,null,null,3.6,"FI-Block Vigi C120, 3p, 30mA, Typ A si"]
["FI-Block","FI-Block Vigi C120, 3p, 300mA, Typ A si","A9N18595",null,"Schneider",125,3.6,null,null,3.6,"FI-Block Vigi C120, 3p, 300mA, Typ A si"]
["FI-Block","FI-Block Vigi C120, 4p, 300mA, Typ A si","A9N18598",null,"Schneider",125,3.6,null,null,3.6,"FI-Block Vigi C120, 4p, 300mA, Typ A si"]
["FI-Block","FI-Block Vigi C120, 4p, 500mA, Typ A si","A9N18599",null,"Schneider",125,3.6,null,null,3.6,"FI-Block Vigi C120, 4p, 500mA, Typ A si"]
["FI-Block","FI-Block Vigi iC60L, 2p, 25A, 100mA, Typ A","A9V22225",null,"Schneider",25,1.1000000000000001,null,null,{"$f":"G2082+I2082","v":1.1000000000000001},"FI-Block Vigi iC60L, 2p, 25A, 100mA, Typ A"]
["FI-Block","FI-Block Vigi iC60L, 2p, 63A, 100mA, Typ A","A9V22263",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60L, 2p, 63A, 100mA, Typ A"]
["FI-Block","FI-Block Vigi iC60L, 3p, 25A, 100mA, Typ A","A9V22325",null,"Schneider",25,1.1000000000000001,null,null,1.1000000000000001,"FI-Block Vigi iC60L, 3p, 25A, 100mA, Typ A"]
["FI-Block","FI-Block Vigi iC60L, 4p, 25A, 100mA, Typ A","A9V22425",null,"Schneider",25,1.1000000000000001,null,null,1.1000000000000001,"FI-Block Vigi iC60L, 4p, 25A, 100mA, Typ A"]
["FI-Block","FI-Block Vigi iC60L, 4p, 63A, 100mA, Typ A","A9V22463",null,"Schneider",63,2.2999999999999998,null,null,{"$f":"G2086+I2086","v":2.2999999999999998},"FI-Block Vigi iC60L, 4p, 63A, 100mA, Typ A"]
["FI-Block","FI-Block Vigi iC60L, 2p, 63A, 300mA, Typ A selekti v","A9V25263",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60L, 2p, 63A, 300mA, Typ A selekti v"]
["FI-Block","FI-Block Vigi iC60L, 3p, 63A, 300mA, Typ A selekti v","A9V25363",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60L, 3p, 63A, 300mA, Typ A selekti v"]
["FI-Block","FI-Block Vigi iC60L, 4p, 63A, 300mA, Typ A selekti v","A9V25463",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60L, 4p, 63A, 300mA, Typ A selekti v"]
["FI-Block","FI-Block Vigi iC60L, 2p, 25A, 500mA, Typ A","A9V26225",null,"Schneider",25,1.1000000000000001,null,null,1.1000000000000001,"FI-Block Vigi iC60L, 2p, 25A, 500mA, Typ A"]
["FI-Block","FI-Block Vigi iC60L, 2p, 63A, 500mA, Typ A","A9V26263",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60L, 2p, 63A, 500mA, Typ A"]
["FI-Block","FI-Block Vigi iC60L, 3p, 25A, 500mA, Typ A","A9V26325",null,"Schneider",25,1.1000000000000001,null,null,1.1000000000000001,"FI-Block Vigi iC60L, 3p, 25A, 500mA, Typ A"]
["FI-Block","FI-Block Vigi iC60L, 3p, 63A, 500mA, Typ A","A9V26363",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60L, 3p, 63A, 500mA, Typ A"]
["FI-Block","FI-Block Vigi iC60L, 4p, 25A, 500mA, Typ A","A9V26425",null,"Schneider",25,1.1000000000000001,null,null,1.1000000000000001,"FI-Block Vigi iC60L, 4p, 25A, 500mA, Typ A"]
["FI-Block","FI-Block Vigi iC60L, 4p, 63A, 500mA, Typ A","A9V26463",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60L, 4p, 63A, 500mA, Typ A"]
["FI-Block","FI-Block Vigi iC60L, 2p, 63A, 1000mA, Typ A selekt iv","A9V29263",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60L, 2p, 63A, 1000mA, Typ A selekt iv"]
["FI-Block","FI-Block Vigi iC60L, 3p, 63A, 1000mA, Typ A selekt iv","A9V29363",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60L, 3p, 63A, 1000mA, Typ A selekt iv"]
["FI-Block","FI-Block Vigi iC60L, 4p, 63A, 1000mA, Typ A selekt iv","A9V29463",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60L, 4p, 63A, 1000mA, Typ A selekt iv"]
["FI-Block","FI-Block Vigi iC60L, 2p, 25A, 10mA, Typ A, SI","A9V30225",null,"Schneider",25,3,null,null,3,"FI-Block Vigi iC60L, 2p, 25A, 10mA, Typ A, SI"]
["FI-Block","FI-Block Vigi iC60L, 2p, 63A, 1000mA, Typ A selekt iv, SI","A9V39263",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60L, 2p, 63A, 1000mA, Typ A selekt iv, SI"]
["FI-Block","FI-Block Vigi iC60L, 3p, 63A, 1000mA, Typ A selekt iv, SI","A9V39363",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60L, 3p, 63A, 1000mA, Typ A selekt iv, SI"]
["FI-Block","FI-Block Vigi iC60L, 4p, 63A, 1000mA, Typ A selekt iv, SI","A9V39463",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60L, 4p, 63A, 1000mA, Typ A selekt iv, SI"]
["FI-Block","FI-Block Vigi iC60L, 2p, 25A, 30mA, Typ A","A9V51225",null,"Schneider",25,1.4,null,null,1.4,"FI-Block Vigi iC60L, 2p, 25A, 30mA, Typ A"]
["FI-Block","FI-Block Vigi iC60L, 2p, 63A, 30mA, Typ A","A9V51263",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60L, 2p, 63A, 30mA, Typ A"]
["FI-Block","FI-Block Vigi iC60L, 3p, 25A, 30mA, Typ A","A9V51325",null,"Schneider",25,1.4,null,null,1.4,"FI-Block Vigi iC60L, 3p, 25A, 30mA, Typ A"]
["FI-Block","FI-Block Vigi iC60L, 3p, 63A, 30mA, Typ A","A9V51363",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60L, 3p, 63A, 30mA, Typ A"]
["FI-Block","FI-Block Vigi iC60L, 4p, 25A, 30mA, Typ A","A9V51425",null,"Schneider",25,1.4,null,null,1.4,"FI-Block Vigi iC60L, 4p, 25A, 30mA, Typ A"]
["FI-Block","FI-Block Vigi iC60L, 4p, 63A, 30mA, Typ A","A9V51463",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60L, 4p, 63A, 30mA, Typ A"]
["FI-Block","FI-Block Vigi iC60L, 2p, 25A, 300mA, Typ A","A9V54225",null,"Schneider",25,1.3,null,null,1.3,"FI-Block Vigi iC60L, 2p, 25A, 300mA, Typ A"]
["FI-Block","FI-Block Vigi iC60L, 2p, 63A, 300mA, Typ A","A9V54263",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60L, 2p, 63A, 300mA, Typ A"]
["FI-Block","FI-Block Vigi iC60L, 3p, 25A, 300mA, Typ A","A9V54325",null,"Schneider",25,1.3,null,null,1.3,"FI-Block Vigi iC60L, 3p, 25A, 300mA, Typ A"]
["FI-Block","FI-Block Vigi iC60L, 3p, 63A, 300mA, Typ A","A9V54363",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60L, 3p, 63A, 300mA, Typ A"]
["FI-Block","FI-Block Vigi iC60L, 4p, 25A, 300mA, Typ A","A9V54425",null,"Schneider",25,1.3,null,null,1.3,"FI-Block Vigi iC60L, 4p, 25A, 300mA, Typ A"]
["FI-Block","FI-Block Vigi iC60L, 4p, 63A, 300mA, Typ A","A9V54463",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60L, 4p, 63A, 300mA, Typ A"]
["FI-Block","FI-Block Vigi iC60L, 2p, 25A, 30mA, Typ A, SI","A9V61225",null,"Schneider",25,1.3,null,null,1.3,"FI-Block Vigi iC60L, 2p, 25A, 30mA, Typ A, SI"]
["FI-Block","FI-Block Vigi iC60L, 2p, 40A, 30mA, Typ A, SI","A9V61240",null,"Schneider",40,1.5,null,null,1.5,"FI-Block Vigi iC60L, 2p, 40A, 30mA, Typ A, SI"]
["FI-Block","FI-Block Vigi iC60L, 2p, 63A, 30mA, Typ A, SI","A9V61263",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60L, 2p, 63A, 30mA, Typ A, SI"]
["FI-Block","FI-Block Vigi iC60L, 3p, 25A, 30mA, Typ A, SI","A9V61325",null,"Schneider",25,1.4,null,null,1.4,"FI-Block Vigi iC60L, 3p, 25A, 30mA, Typ A, SI"]
["FI-Block","FI-Block Vigi iC60L, 3p, 40A, 30mA, Typ A, SI","A9V61340",null,"Schneider",40,1.5,null,null,1.5,"FI-Block Vigi iC60L, 3p, 40A, 30mA, Typ A, SI"]
["FI-Block","FI-Block Vigi iC60L, 3p, 63A, 30mA, Typ A, SI","A9V61363",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60L, 3p, 63A, 30mA, Typ A, SI"]
["FI-Block","FI-Block Vigi iC60L, 4p, 25A, 30mA, Typ A, SI","A9V61425",null,"Schneider",25,1.4,null,null,1.4,"FI-Block Vigi iC60L, 4p, 25A, 30mA, Typ A, SI"]
["FI-Block","FI-Block Vigi iC60L, 4p, 40A, 30mA, Typ A, SI","A9V61440",null,"Schneider",40,1.5,null,null,1.5,"FI-Block Vigi iC60L, 4p, 40A, 30mA, Typ A, SI"]
["FI-Block","FI-Block Vigi iC60L, 4p, 63A, 30mA, Typ A, SI","A9V61463",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60L, 4p, 63A, 30mA, Typ A, SI"]
["FI-Block","FI-Block Vigi iC60L, 2p, 63A, 300mA, Typ A selekti v, SI","A9V65263",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60L, 2p, 63A, 300mA, Typ A selekti v, SI"]
["FI-Block","FI-Block Vigi iC60L, 3p, 63A, 300mA, Typ A selekti v, SI","A9V65363",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60L, 3p, 63A, 300mA, Typ A selekti v, SI"]
["FI-Block","FI-Block Vigi iC60L, 4p, 63A, 300mA, Typ A selekti v, SI","A9V65463",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60L, 4p, 63A, 300mA, Typ A selekti v, SI"]
["FI-Block","FI-Block Vigi iC60N/H, 2p, 25A, 30mA, Typ A","A9W21225",null,"Schneider",25,1.4,null,null,1.4,"FI-Block Vigi iC60N/H, 2p, 25A, 30mA, Typ A"]
["FI-Block","FI-Block Vigi iC60N/H, 2p, 63A, 30mA, Typ A","A9W21263",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60N/H, 2p, 63A, 30mA, Typ A"]
["FI-Block","FI-Block Vigi iC60N/H, 3p, 25A, 30mA, Typ A","A9W21325",null,"Schneider",25,1.4,null,null,1.4,"FI-Block Vigi iC60N/H, 3p, 25A, 30mA, Typ A"]
["FI-Block","FI-Block Vigi iC60N/H, 3p, 63A, 30mA, Typ A","A9W21363",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60N/H, 3p, 63A, 30mA, Typ A"]
["FI-Block","FI-Block Vigi iC60N/H, 4p, 25A, 30mA, Typ A","A9W21425",null,"Schneider",25,1.4,null,null,1.4,"FI-Block Vigi iC60N/H, 4p, 25A, 30mA, Typ A"]
["FI-Block","FI-Block Vigi iC60N/H, 4p, 63A, 30mA, Typ A","A9W21463",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60N/H, 4p, 63A, 30mA, Typ A"]
["FI-Block","FI-Block Vigi iC60N/H, 2p, 25A, 100mA, Typ A","A9W22225",null,"Schneider",25,1.1000000000000001,null,null,1.1000000000000001,"FI-Block Vigi iC60N/H, 2p, 25A, 100mA, Typ A"]
["FI-Block","FI-Block Vigi iC60N/H, 4p, 25A, 100mA, Typ A","A9W22425",null,"Schneider",25,1.1000000000000001,null,null,1.1000000000000001,"FI-Block Vigi iC60N/H, 4p, 25A, 100mA, Typ A"]
["FI-Block","FI-Block Vigi iC60N/H, 4p, 63A, 100mA, Typ A","A9W22463",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60N/H, 4p, 63A, 100mA, Typ A"]
["FI-Block","FI-Block Vigi iC60N/H, 2p, 25A, 300mA, Typ A","A9W24225",null,"Schneider",25,1.3,null,null,1.3,"FI-Block Vigi iC60N/H, 2p, 25A, 300mA, Typ A"]
["FI-Block","FI-Block Vigi iC60N/H, 2p, 63A, 300mA, Typ A","A9W24263",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60N/H, 2p, 63A, 300mA, Typ A"]
["FI-Block","FI-Block Vigi iC60N/H, 3p, 25A, 300mA, Typ A","A9W24325",null,"Schneider",25,1.3,null,null,1.3,"FI-Block Vigi iC60N/H, 3p, 25A, 300mA, Typ A"]
["FI-Block","FI-Block Vigi iC60N/H, 3p, 63A, 300mA, Typ A","A9W24363",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60N/H, 3p, 63A, 300mA, Typ A"]
["FI-Block","FI-Block Vigi iC60N/H, 4p, 25A, 300mA, Typ A","A9W24425",null,"Schneider",25,1.3,null,null,1.3,"FI-Block Vigi iC60N/H, 4p, 25A, 300mA, Typ A"]
["FI-Block","FI-Block Vigi iC60N/H, 4p, 63A, 300mA, Typ A","A9W24463",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60N/H, 4p, 63A, 300mA, Typ A"]
["FI-Block","FI-Block Vigi iC60N/H, 2p, 63A, 300mA, Typ A selek tiv","A9W25263",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60N/H, 2p, 63A, 300mA, Typ A selek tiv"]
["FI-Block","FI-Block Vigi iC60N/H, 3p, 63A, 300mA, Typ A selek tiv","A9W25363",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60N/H, 3p, 63A, 300mA, Typ A selek tiv"]
["FI-Block","FI-Block Vigi iC60N/H, 4p, 63A, 300mA, Typ A selek tiv","A9W25463",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60N/H, 4p, 63A, 300mA, Typ A selek tiv"]
["FI-Block","FI-Block Vigi iC60N/H, 2p, 25A, 500mA, Typ A","A9W26225",null,"Schneider",25,1.1000000000000001,null,null,1.1000000000000001,"FI-Block Vigi iC60N/H, 2p, 25A, 500mA, Typ A"]
["FI-Block","FI-Block Vigi iC60N/H, 2p, 63A, 500mA, Typ A","A9W26263",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60N/H, 2p, 63A, 500mA, Typ A"]
["FI-Block","FI-Block Vigi iC60N/H, 3p, 25A, 500mA, Typ A","A9W26325",null,"Schneider",25,1.1000000000000001,null,null,1.1000000000000001,"FI-Block Vigi iC60N/H, 3p, 25A, 500mA, Typ A"]
["FI-Block","FI-Block Vigi iC60N/H, 3p, 63A, 500mA, Typ A","A9W26363",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60N/H, 3p, 63A, 500mA, Typ A"]
["FI-Block","FI-Block Vigi iC60N/H, 4p, 25A, 500mA, Typ A","A9W26425",null,"Schneider",25,1.1000000000000001,null,null,1.1000000000000001,"FI-Block Vigi iC60N/H, 4p, 25A, 500mA, Typ A"]
["FI-Block","FI-Block Vigi iC60N/H, 4p, 63A, 500mA, Typ A","A9W26463",null,"Schneider",63,2.2999999999999998,null,null,{"$f":"G2150+I2150","v":2.2999999999999998},"FI-Block Vigi iC60N/H, 4p, 63A, 500mA, Typ A"]
["FI-Block","FI-Block Vigi iC60N/H, 2p, 25A, 10mA, Typ A, SI","A9W30225",null,"Schneider",25,3,null,null,3,"FI-Block Vigi iC60N/H, 2p, 25A, 10mA, Typ A, SI"]
["FI-Block","FI-Block Vigi iC60N/H, 2p, 25A, 30mA, Typ A, SI","A9W31225",null,"Schneider",25,1.4,null,null,1.4,"FI-Block Vigi iC60N/H, 2p, 25A, 30mA, Typ A, SI"]
["FI-Block","FI-Block Vigi iC60N/H, 2p, 63A, 30mA, Typ A, SI","A9W31263",null,"Schneider",25,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60N/H, 2p, 63A, 30mA, Typ A, SI"]
["FI-Block","FI-Block Vigi iC60N/H, 3p, 25A, 30mA, Typ A, SI","A9W31325",null,"Schneider",63,1.4,null,null,1.4,"FI-Block Vigi iC60N/H, 3p, 25A, 30mA, Typ A, SI"]
["FI-Block","FI-Block Vigi iC60N/H, 3p, 63A, 30mA, Typ A, SI","A9W31363",null,"Schneider",25,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60N/H, 3p, 63A, 30mA, Typ A, SI"]
["FI-Block","FI-Block Vigi iC60N/H, 4p, 25A, 30mA, Typ A, SI","A9W31425",null,"Schneider",63,1.4,null,null,1.4,"FI-Block Vigi iC60N/H, 4p, 25A, 30mA, Typ A, SI"]
["FI-Block","FI-Block Vigi iC60N/H, 4p, 63A, 30mA, Typ A, SI","A9W31463",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60N/H, 4p, 63A, 30mA, Typ A, SI"]
["FI-Block","FI-Block Vigi iC60N/H, 2p, 63A, 300mA, Typ A selek tiv, SI","A9W35263",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60N/H, 2p, 63A, 300mA, Typ A selek tiv, SI"]
["FI-Block","FI-Block Vigi iC60N/H, 3p, 63A, 300mA, Typ A selek tiv, SI","A9W35363",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60N/H, 3p, 63A, 300mA, Typ A selek tiv, SI"]
["FI-Block","FI-Block Vigi iC60N/H, 4p, 63A, 300mA, Typ A selek tiv, SI","A9W35463",null,"Schneider",63,2.2999999999999998,null,null,2.2999999999999998,"FI-Block Vigi iC60N/H, 4p, 63A, 300mA, Typ A selek tiv, SI"]
["FI-Block","FI-Block Vigi C120, 4p, 30mA, Typ A si","A9N18597",null,"Schneider",125,3.6,null,null,3.6,"FI-Block Vigi C120, 4p, 30mA, Typ A si"]
[]
[null,"Motorschutzschalter"]
["Motorschutzschalter","Motorschutzschalter P25M, 3p, 10A Schutz für Wechsel-/Drehstrommotoren",21109,null,"Schneider",10,2.5,null,null,2.5,"Motorschutzschalter P25M, 3p, 10A Schutz für Wechsel-/Drehstrommotoren"]
["Motorschutzschalter","Motorschutzschalter P25M, 3p, 10A Schutz für Wechsel-/Drehstrommotoren","E-21109",null,"Schneider",10,2.5,null,null,2.5,"Motorschutzschalter P25M, 3p, 10A Schutz für Wechsel-/Drehstrommotoren"]
[]
["Drucktaster","Drucktaster"]
["Drucktaster","Drucktaster iPB -1S, 20A grau","A9E18032",null,"Schneider",20,0.6,null,null,{"$f":"G2168+I2168","v":0.6},"Drucktaster iPB -1S, 20A grau"]
["Drucktaster","Drucktaster iPB, 1 Schließer + 1 Öffner, Taste grau","A9E18033",null,"Schneider",20,0.6,null,null,0.6,"Drucktaster iPB, 1 Schließer + 1 Öffner, Taste grau"]
["Drucktaster","Drucktaster iPB, 1S, grau, LED grün 110-230VAC","A9E18036",null,"Schneider",20,0.6,null,null,0.6,"Drucktaster iPB, 1S, grau, LED grün 110-230VAC"]
["Drucktaster","Drucktaster iPB, 1S, grau, LED grün 12-48V AC/DC","A9E18038",null,"Schneider",20,0.6,null,null,0.6,"Drucktaster iPB, 1S, grau, LED grün 12-48V AC/DC"]
["Drucktaster","Doppel-Drucktaster iPB, 1S-1Ö, grün/rot","A9E18034",null,"Schneider",20,0.6,null,null,{"$f":"G2172+I2172","v":0.6},"Doppel-Drucktaster iPB, 1S-1Ö, grün/rot"]
["Drucktaster","Doppel-Drucktaster iPB, 1S-1S, grau/grau","A9E18035",null,"Schneider",20,0.6,null,null,{"$f":"G2173+I2173","v":0.6},"Doppel-Drucktaster iPB, 1S-1S, grau/grau"]
["Drucktaster","Drucktaster iPB, 1Ö, grau, LED rot 110-230VAC","A9E18037",null,"Schneider",20,0.6,null,null,{"$f":"G2174+I2174","v":0.6},"Drucktaster iPB, 1Ö, grau, LED rot 110-230VAC"]
["Drucktaster","Drucktaster iPB, 1Ö, grau, LED rot 12-48V AC/DC","A9E18039",null,"Schneider",20,0.6,null,null,{"$f":"G2175+I2175","v":0.6},"Drucktaster iPB, 1Ö, grau, LED rot 12-48V AC/DC"]
["Drucktaster","Leuchtdrucktaster, rot, flach,1S+1Ö, tastend, +BA 9s 250V 2,4W","XB5AW3465",null,"Schneider",10,2.4,null,null,{"$f":"G2176+I2176","v":2.4},"Leuchtdrucktaster, rot, flach,1S+1Ö, tastend, +BA 9s 250V 2,4W"]
["Drucktaster","Steuerungstaster komplett NOT- AUS rastend Drehentriegelung 1S + 1Ö","XB4BS8445",null,"Schneider",10,2.4,null,null,{"$f":"G2177+I2177","v":2.4},"Steuerungstaster komplett NOT- AUS rastend Drehentriegelung 1S + 1Ö"]
[]
[null,"Wechselschalter "]
["Wechselschalter ","Wechselschalter iSSW, 1W, 20A, 250VAC, 2 Positione n","A9E18070",null,"Schneider",20,0.8,null,null,0.8,"Wechselschalter iSSW, 1W, 20A, 250VAC, 2 Positione n"]
["Wechselschalter ","Wechselschalter iSSW, 2W, 20A, 250VAC, 2 Positionen","A9E18071",null,"Schneider",20,0.8,null,null,0.8,"Wechselschalter iSSW, 2W, 20A, 250VAC, 2 Positionen"]
["Wechselschalter ","Wechselschalter iSSW, 1S+1Ö, 20A, 250VAC, 2 Positi onen","A9E18072",null,"Schneider",20,0.8,null,null,0.8,"Wechselschalter iSSW, 1S+1Ö, 20A, 250VAC, 2 Positi onen"]
["Wechselschalter ","Gruppenschalter iSSW, 1W, 20A, 250V AC, 3 Position 1-0-2","A9E18073",null,"Schneider",20,0.8,null,null,0.8,"Gruppenschalter iSSW, 1W, 20A, 250V AC, 3 Position 1-0-2"]
[]
[null,"Leuchtmelder"]
["Leuchtmelder","Leuchtmelder iIL, LED, rot, 110-230 V AC","A9E18320",null,"Schneider","-",0.3,null,null,0.3,"Leuchtmelder iIL, LED, rot, 110-230 V AC"]
["Leuchtmelder","Leuchtmelder iIL, LED, grün, 110-230 V AC","A9E18321",null,"Schneider","-",0.3,null,null,0.3,"Leuchtmelder iIL, LED, grün, 110-230 V AC"]
["Leuchtmelder","Leuchtmelder iIL, LED, weiß, 110-230 V AC","A9E18322",null,"Schneider","-",0.3,null,null,0.3,"Leuchtmelder iIL, LED, weiß, 110-230 V AC"]
["Leuchtmelder","Dreiphasen-Leuchtmelder iIL, LED, rot, 230-400V AC","A9E18327",null,"Schneider","-",0.3,null,null,0.3,"Dreiphasen-Leuchtmelder iIL, LED, rot, 230-400V AC"]
["Leuchtmelder","Leuchtmelder iIL, LED, blau, 110-230 V AC","A9E18323",null,"Schneider","-",0.3,null,null,{"$f":"G2190+I2190","v":0.3},"Leuchtmelder iIL, LED, blau, 110-230 V AC"]
["Leuchtmelder","Leuchtmelder iIL, LED, gelb, 110-230 V AC","A9E18324",null,"Schneider","-",0.3,null,null,0.3,"Leuchtmelder iIL, LED, gelb, 110-230 V AC"]
["Leuchtmelder","Doppel-Leuchtmelder iIL, LED, grün/rot, 110-230V A C","A9E18325",null,"Schneider","-",0.6,null,null,0.6,"Doppel-Leuchtmelder iIL, LED, grün/rot, 110-230V A C"]
["Leuchtmelder","Blinkleuchtmelder iIL, LED, rot, 110-230V AC","A9E18326",null,"Schneider","-",0.3,null,null,0.3,"Blinkleuchtmelder iIL, LED, rot, 110-230V AC"]
["Leuchtmelder","Doppel-Leuchtmelder iIL, LED, weiß/weiß, 110-230V  AC","A9E18328",null,"Schneider","-",0.6,null,null,0.6,"Doppel-Leuchtmelder iIL, LED, weiß/weiß, 110-230V  AC"]
["Leuchtmelder","Leuchtmelder iIL, LED, rot, 12-48 V AC/DC","A9E18330",null,"Schneider","-",0.3,null,null,0.3,"Leuchtmelder iIL, LED, rot, 12-48 V AC/DC"]
["Leuchtmelder","Leuchtmelder iIL, LED, grün, 12-48 V AC/DC","A9E18331",null,"Schneider","-",0.3,null,null,0.3,"Leuchtmelder iIL, LED, grün, 12-48 V AC/DC"]
["Leuchtmelder","Leuchtmelder iIL, LED, weiß, 12-48 V AC/DC","A9E18332",null,"Schneider","-",0.3,null,null,0.3,"Leuchtmelder iIL, LED, weiß, 12-48 V AC/DC"]
["Leuchtmelder","Leuchtmelder iIL, LED, blau, 12-48 V AC/DC","A9E18333",null,"Schneider","-",0.3,null,null,0.3,"Leuchtmelder iIL, LED, blau, 12-48 V AC/DC"]
["Leuchtmelder","Leuchtmelder iIL, LED, gelb, 12-48 V AC/DC","A9E18334",null,"Schneider","-",0.3,null,null,0.3,"Leuchtmelder iIL, LED, gelb, 12-48 V AC/DC"]
["Leuchtmelder","Doppel-Leuchtmelder iIL, LED, grün/rot, 12-48V AC/ DC","A9E18335",null,"Schneider","-",0.6,null,null,0.6,"Doppel-Leuchtmelder iIL, LED, grün/rot, 12-48V AC/ DC"]
[]
[null,"Puffermodul/Spannungsquelle"]
["Puffermodul/Spannungsquelle","Puffermodul, 24-28,8 VDC, 40 A, für Spannungsversorgung ABL8","ABL8BUF24400",null,"Schneider",40,15,null,null,{"$f":"G2203+I2203","v":15},"Puffermodul, 24-28,8 VDC, 40 A, für Spannungsversorgung ABL8"]
["Puffermodul/Spannungsquelle","Spannungsversorgung 230V / 24VDC 3A 100-500 VAC, 1-2 P, 24 VDC, 72 W","ABL8RPS24030",null,"Schneider",3,7.8,null,null,7.8,"Spannungsversorgung 230V / 24VDC 3A 100-500 VAC, 1-2 P, 24 VDC, 72 W"]
["Puffermodul/Spannungsquelle","Spannungsversorgung 240V 24VDC 1,2A 100-240VAC 30W modular getaktet","ABLM1A24012",null,"Schneider",1.25,5,null,null,5,"Spannungsversorgung 240V 24VDC 1,2A 100-240VAC 30W modular getaktet"]
["Puffermodul/Spannungsquelle","Spannungsversorgung 230V / 24VDC 2,5A 100-240VAC, 1-2 P, 60 W Getaktete, MODULAR","ABLM1A24025",null,"Schneider",2.5,6.5,null,null,6.5,"Spannungsversorgung 230V / 24VDC 2,5A 100-240VAC, 1-2 P, 60 W Getaktete, MODULAR"]
["Puffermodul/Spannungsquelle","Getaktete Spannungsversorgung, OPTIMUM, 100-240VAC  12VDC, 6,2A, 75W, 1-phasig","ABLS1A12062",null,"Schneider",6.2,16,null,null,16,"Getaktete Spannungsversorgung, OPTIMUM, 100-240VAC  12VDC, 6,2A, 75W, 1-phasig"]
["Puffermodul/Spannungsquelle","Getaktete Spannungsversorgung, OPTIMUM, 100-240VAC 24VDC, 3,8A, 90W, 1-phasig","ABLS1A24038",null,"Schneider",3.8,13,null,null,13,"Getaktete Spannungsversorgung, OPTIMUM, 100-240VAC 24VDC, 3,8A, 90W, 1-phasig"]
["Puffermodul/Spannungsquelle","Getaktete Spannungsversorgung, OPTIMUM, 100-240VAC 24VDC, 5A, 120W, 1-phasig","ABLS1A24050",null,"Schneider",5,25,null,null,25,"Getaktete Spannungsversorgung, OPTIMUM, 100-240VAC 24VDC, 5A, 120W, 1-phasig"]
[]
["Dämmerungsschalter ","Dämmerungsschalter "]
["Dämmerungsschalter ","Dämmerungsschalter IC Astro, Bluetooth","CCT15225",null,"Schneider",16,0.5,null,null,0.5,"Dämmerungsschalter IC Astro, Bluetooth"]
["Dämmerungsschalter ","Dämmerungsschalter IC Astro, Bluetooth","CCT15245",null,"Schneider",16,0.5,null,null,0.5,"Dämmerungsschalter IC Astro, Bluetooth"]
["Dämmerungsschalter ","Dämmerungsschalter IC100, 1 Schließer, 1TE","CCT15482",null,"Schneider",16,0.5,null,null,{"$f":"G2214+I2214","v":0.5},"Dämmerungsschalter IC100, 1 Schließer, 1TE"]
["Dämmerungsschalter ","DÄMMERUNGSSCHALTER, IC100KP+, 1 KANAL","CCT15494",null,"Schneider",16,0.8,null,null,{"$f":"G2215+I2215","v":0.8},"DÄMMERUNGSSCHALTER, IC100KP+, 1 KANAL"]
[]
["Motorschutzschalter","Motorschutzschalter"]
["Motorschutzschalter","Motorschutzschalter, 3p, 1-1,6A Tasterbetätigung, Schraubanschluss","GV2ME06",null,"Schneider",1.6,2.5,null,null,{"$f":"G2218+I2218","v":2.5},"Motorschutzschalter, 3p, 1-1,6A Tasterbetätigung, Schraubanschluss"]
["Motorschutzschalter","Motorschutzschalter, 3p, 1,6-2,5A Tasterbetätigung, Schraubanschluss","GV2ME07",null,"Schneider",2.5,2.5,null,null,2.5,"Motorschutzschalter, 3p, 1,6-2,5A Tasterbetätigung, Schraubanschluss"]
["Motorschutzschalter","Motorschutzschalter, 3p, 4-6,3A Tasterbetätigung, Schraubanschluss","GV2ME10",null,"Schneider",6.3,2.5,null,null,2.5,"Motorschutzschalter, 3p, 4-6,3A Tasterbetätigung, Schraubanschluss"]
["Motorschutzschalter","Motorschutzschalter, 3p, 9-14A Tasterbetätigung, Schraubanschluss","GV2ME16",null,"Schneider",14,2.5,null,null,2.5,"Motorschutzschalter, 3p, 9-14A Tasterbetätigung, Schraubanschluss"]
[]
["Dimmer ","Dimmer "]
["Dimmer ","Dimmer STD1000RL-DIN, 1000 W","CCTDD20003",null,"Schneider","-",3,null,null,{"$f":"G2224+I2224","v":3},"Dimmer STD1000RL-DIN, 1000 W"]
["Dimmer ","Dimmer STD1000RL-SAE, 1000 W","CCTDD20004",null,"Schneider","-",3,null,null,3,"Dimmer STD1000RL-SAE, 1000 W"]
["Dimmer ","Dimmer SCU10-DIN, 1-10V","CCTDD20011",null,"Schneider","-",3,null,null,3,"Dimmer SCU10-DIN, 1-10V"]
["Dimmer ","Dimmer SCU10-SAE, 1-10V","CCTDD20012",null,"Schneider","-",3,null,null,3,"Dimmer SCU10-SAE, 1-10V"]
["Dimmer ","Acti 9, STD400LED DIN Universaldimmer","CCTDD20016",null,"Schneider","-",3,null,null,3,"Acti 9, STD400LED DIN Universaldimmer"]
["Dimmer ","Acti 9, STD400LED+DIN Universaldimmer","CCTDD20017",null,"Schneider","-",3,null,null,3,"Acti 9, STD400LED+DIN Universaldimmer"]
[]
["EVLink Lastmanagement","EVLink Lastmanagement"]
["EVLink Lastmanagement","EVLink Lastmanagement 5 LS dynamisch","HMIBSCEA53D1EDB",null,"Schneider","-",16,null,null,16,"EVLink Lastmanagement 5 LS dynamisch"]
["EVLink Lastmanagement","EVlink Lastmanagement 100 LS dynamisch","HMIBSCEA53D1EDL",null,"Schneider","-",16,null,null,16,"EVlink Lastmanagement 100 LS dynamisch"]
["EVLink Lastmanagement","EVlink dynamisches Lastmanagement für max. 50  Ladesäulen","HMIBSCEA53D1EDM",null,"Schneider","-",16,null,null,16,"EVlink dynamisches Lastmanagement für max. 50  Ladesäulen"]
["EVLink Lastmanagement","EVLink Lastmanagement 15 LS dynamisch","HMIBSCEA53D1EDS",null,"Schneider","-",16,null,null,16,"EVLink Lastmanagement 15 LS dynamisch"]
["EVLink Lastmanagement","EVLink Lastmanagement 15 LS statisch","HMIBSCEA53D1ESS",null,"Schneider","-",16,null,null,16,"EVLink Lastmanagement 15 LS statisch"]
[]
["Leistungsschütz","Leistungsschütz"]
["Leistungsschütz","Leistungsschütz 200A AC1 4p, Spule 24 V DC","LC1D115004BD",null,"Schneider",200,24,null,null,24,"Leistungsschütz 200A AC1 4p, Spule 24 V DC"]
["Leistungsschütz","SCHÜTZ 4P 200A 230V50/60HZ 4p ohne Hilfsschalter 2S / 2Ö","LC1D115004P7",null,"Schneider",200,24,null,null,24,"SCHÜTZ 4P 200A 230V50/60HZ 4p ohne Hilfsschalter 2S / 2Ö"]
["Leistungsschütz","Leistungsschütz, 3p+1S+1Ö, 37kW/400V/AC3 80A, Spule 230V 50/60Hz","LC1D80P7",null,"Schneider",80,12.5,null,null,12.5,"Leistungsschütz, 3p+1S+1Ö, 37kW/400V/AC3 80A, Spule 230V 50/60Hz"]
["Leistungsschütz","Leistungsschütz, 4p+1S+1Ö, 80A/AC1,  Spule24V DC","LC1DT80A3BD",null,"Schneider",80,10.199999999999999,null,null,10.199999999999999,"Leistungsschütz, 4p+1S+1Ö, 80A/AC1,  Spule24V DC"]
[]
[null,"Modicon"]
["Modicon","Modicon Managed Switch, 8 Ports für Kupfer (8TX 10/100 Mbit/s)","MCSESM083F23F0",null,"Schneider","-",6,null,null,{"$f":"G2245+I2245","v":6},"Modicon Managed Switch, 8 Ports für Kupfer (8TX 10/100 Mbit/s)"]
["Modicon","Modicon Unmanaged Switch, 4 Ports für Kupfer (4TX  Port für Glasfaser Multimode (1FX-MM 100 Mbit/s)","MCSESU053F1CU0",null,"Schneider","-",2.4,null,null,2.4,"Modicon Unmanaged Switch, 4 Ports für Kupfer (4TX  Port für Glasfaser Multimode (1FX-MM 100 Mbit/s)"]
["Modicon","Connexium Ethernet Switch 5 ports 10/100","MCSESU053FN0",null,"Schneider","-",1.3,null,null,1.3,"Connexium Ethernet Switch 5 ports 10/100"]
["Modicon","Modicon Unmanaged Switch - 8 ports for copper","MCSESU083FN0",null,"Schneider","-",1.5,null,null,1.5,"Modicon Unmanaged Switch - 8 ports for copper"]
[]
["Fehlerstrom-Schutzrelais","Fehlerstrom-Schutzrelais"]
["Fehlerstrom-Schutzrelais","Fehlerstrom-Schutzrelais Vigirex rh197m 230V AC",56517,null,"Schneider",30,4,null,null,4,"Fehlerstrom-Schutzrelais Vigirex rh197m 230V AC"]
["Fehlerstrom-Schutzrelais","Fehlerstromschutzrelais, VigiPacT RHB, Typ B, 30mA 100-250VAC/DC, DIN-Schienenmontage","LV481010",null,"Schneider",5,6.5,null,null,6.5,"Fehlerstromschutzrelais, VigiPacT RHB, Typ B, 30mA 100-250VAC/DC, DIN-Schienenmontage"]
[]
["Koppelrelais","Koppelrelais"]
["Koppelrelais","Koppelrelais Niederspannungssignal iRBN, 5mA/5VAC- DC, 2A/250VCA, 230VAC","A9A15393",null,"Schneider",2,2.5,null,null,2.5,"Koppelrelais Niederspannungssignal iRBN, 5mA/5VAC- DC, 2A/250VCA, 230VAC"]
["Koppelrelais","Koppelrelais Kleinspannungssignal iRTBT, 10mA/10VD C, 5A/250VAC, 12-24 VAC/DC","A9A15416",null,"Schneider",5,0.22,null,null,0.22,"Koppelrelais Kleinspannungssignal iRTBT, 10mA/10VD C, 5A/250VAC, 12-24 VAC/DC"]
[]
["PTC-Widerstandsheizung","PTC-Widerstandsheizung"]
["PTC-Widerstandsheizung","ClimaSys-PTC-Widerstandsheizung 100W,110-250V isoliert","NSYCR100WU2C",null,"Schneider","-",100,null,null,100,"ClimaSys-PTC-Widerstandsheizung 100W,110-250V isoliert"]
["PTC-Widerstandsheizung","ClimaSys-PTC-Widerstandsheizung 20W,110-250V  isoliert","NSYCR20WU2C",null,"Schneider","-",20,null,null,20,"ClimaSys-PTC-Widerstandsheizung 20W,110-250V  isoliert"]
[]
["Spannungskontrollrelais/Phasenkontrollrelais","Spannungskontrollrelais/Phasenkontrollrelais"]
["Spannungskontrollrelais/Phasenkontrollrelais","Phasenkontrollrelais iRCP, 8A, 1W, 400V 50/60Hz","A9E21180",null,"Schneider",8,1,null,null,1,"Phasenkontrollrelais iRCP, 8A, 1W, 400V 50/60Hz"]
["Spannungskontrollrelais/Phasenkontrollrelais","Spannungskontrollrelais iRCU, 8A, 230V AC, 1W","A9E21182",null,"Schneider",8,1,null,null,1,"Spannungskontrollrelais iRCU, 8A, 230V AC, 1W"]
[]
[" Logic Controller"," Logic Controller"]
[" Logic Controller","HomeLYnk Logic Controller lichtgrau","LSS100100",null,"Schneider","-",2,null,null,2,"HomeLYnk Logic Controller lichtgrau"]
[" Logic Controller","Logik-Controller spaceLYnk","LSS100200",null,"Schneider","-",2,null,null,2,"Logik-Controller spaceLYnk"]
[]
["Hochleistungsschütz","Hochleistungsschütz"]
["Hochleistungsschütz","Hochleistungsschütz iCT+, 1p+N, 1S, 20A, 230V AC","A9C15030",null,"Schneider",20,1.1000000000000001,null,null,{"$f":"G2271+I2271","v":1.1000000000000001},"Hochleistungsschütz iCT+, 1p+N, 1S, 20A, 230V AC"]
["Hochleistungsschütz","Vorwahl-Hochleistungsschütz iCT+, 1p+N, 1S, 20A, 2 30V AC","A9C15031",null,"Schneider",20,1.1000000000000001,null,null,1.1000000000000001,"Vorwahl-Hochleistungsschütz iCT+, 1p+N, 1S, 20A, 2 30V AC"]
[]
["Impulssteuergerät","Impulssteuergerät"]
["Impulssteuergerät","Impulssteuergerät iACTc, 230-240V AC","A9C18308",null,"Schneider",0.2,3,null,null,3,"Impulssteuergerät iACTc, 230-240V AC"]
["Impulssteuergerät","Impulssteuergerät iACTc, 24-48V AC","A9C18309",null,"Schneider",0.2,3,null,null,3,"Impulssteuergerät iACTc, 24-48V AC"]
[]
["Umschaltrelais","Umschaltrelais"]
["Umschaltrelais","Umschaltrelais iRLI, 1W+1S, 10A, 230V-240V AC","A9E15535",null,"Schneider",10,4,null,null,{"$f":"G2279+I2279","v":4},"Umschaltrelais iRLI, 1W+1S, 10A, 230V-240V AC"]
["Umschaltrelais","Umschaltrelais iRLI, 1W+1S, 10A, 24V AC","A9E15537",null,"Schneider",10,4,null,null,4,"Umschaltrelais iRLI, 1W+1S, 10A, 24V AC"]
["Umschaltrelais","Umschaltrelais iRLI, 1W+1S, 10A, 12V AC","A9E15538",null,"Schneider",10,4,null,null,4,"Umschaltrelais iRLI, 1W+1S, 10A, 12V AC"]
[]
["Kontakterweiterung ","Kontakterweiterung "]
["Kontakterweiterung ","Kontakterweiterung iERL für iRLI -1W+1S, 10A, 230V -240V AC","A9E15539",null,"Schneider",10,8,null,null,8,"Kontakterweiterung iERL für iRLI -1W+1S, 10A, 230V -240V AC"]
["Kontakterweiterung ","Kontakterweiterung iERL für iRLI -1W+1S, 10A, 48V  AC","A9E15540",null,"Schneider",10,8,null,null,8,"Kontakterweiterung iERL für iRLI -1W+1S, 10A, 48V  AC"]
["Kontakterweiterung ","Kontakterweiterung iERL für iRLI -1W+1S, 10A, 24V  AC","A9E15541",null,"Schneider",10,8,null,null,8,"Kontakterweiterung iERL für iRLI -1W+1S, 10A, 24V  AC"]
["Kontakterweiterung ","Kontakterweiterung iERL für iRLI -1W+1S, 10A, 12V  AC","A9E15542",null,"Schneider",10,8,null,null,8,"Kontakterweiterung iERL für iRLI -1W+1S, 10A, 12V  AC"]
[]
["Stromkontrollrelais ","Stromkontrollrelais "]
["Stromkontrollrelais ","Stromkontrollrelais iRCI, 8A, 230V AC, 1W","A9E21181",null,"Schneider",8,2,null,null,{"$f":"G2290+I2290","v":2},"Stromkontrollrelais iRCI, 8A, 230V AC, 1W"]
[]
[null,"Fehlerstromschutz-Zusatzmodul VigiPacT"]
["Fehlerstromschutz-Zusatzmodul VigiPacT","4P 200-440V AC 0.03-10A VIGI MH","LV429489",null,"Schneider",160,1.35,null,null,{"$f":"G2293+I2293","v":1.35},"4P 200-440V AC 0.03-10A VIGI MH"]
["Fehlerstromschutz-Zusatzmodul VigiPacT","3P 200-440V AC 0.03-10A VIGI MH","LV429492",null,"Schneider",250,3.3,null,null,3.3,"3P 200-440V AC 0.03-10A VIGI MH"]
["Fehlerstromschutz-Zusatzmodul VigiPacT","4P 200-440V AC 0.03-10A VIGI MH","LV429493",null,"Schneider",250,3.3,null,null,3.3,"4P 200-440V AC 0.03-10A VIGI MH"]
["Fehlerstromschutz-Zusatzmodul VigiPacT","3P 200-440VAC 0.3-30A VIGI MB","LV432464",null,"Schneider",630,9.3000000000000007,null,null,9.3000000000000007,"3P 200-440VAC 0.3-30A VIGI MB"]
["Fehlerstromschutz-Zusatzmodul VigiPacT","4P 200-440VAC 0.3-30A VIGI MB","LV432465",null,"Schneider",630,9.3000000000000007,null,null,9.3000000000000007,"4P 200-440VAC 0.3-30A VIGI MB"]
[]
["Gruppenschalter","Gruppenschalter"]
["Gruppenschalter","Gruppenschalter iSSW, 2W, 20A, 250V AC, 3 Position en","A9E18074",null,"Schneider",20,0.8,null,null,{"$f":"G2300+I2300","v":0.8},"Gruppenschalter iSSW, 2W, 20A, 250V AC, 3 Position en"]

{"sheet":"Tabelle 4 - Pv_Sammelschiene","index":3,"n_rows":55,"n_cols":17,"rows_kept":55,"cut":false,"hidden":false,"merged":[[46,8,48,8],[50,8,52,8],[23,8,26,8],[28,8,31,8],[33,8,35,8],[37,8,39,8],[41,8,44,8],[1,8,3,8],[5,8,7,8],[9,8,11,8],[13,8,17,8],[19,8,21,8],[50,7,52,7],[1,7,3,7],[5,7,7,7],[9,7,11,7],[13,7,17,7],[19,7,21,7],[23,7,26,7],[28,7,31,7],[33,7,35,7],[37,7,39,7],[41,7,44,7],[46,7,48,7]]}
["Geräteart","Hersteller","Typ / \nBestellnummer","Bemerkung","Bemessungsstrom CU-Schiene\nIn [A]"," Nennstrom CU-Schiene, \nInC [A]","Verlustleistung der CU-Schiene pro Pol bei Nennstrom\n[W]","max. Strom CU-Schiene, Imax [A]\n(Schienentemperatur 90°C)","Verlustleistung der CU-Schiene pro Pol bei max. Strom\n[W]"]
["Sammelschiene je 1m","ABN","12x5","Beim Lüfttemperatur 55°C",125,100,3.5768307322929171,215,17.899999999999999,null,null,"12x5",100,128,200]
["Sammelschiene je 1m","ABN","12x5","Beim Lüfttemperatur 55°C",160,128,9.2808451380552217]
["Sammelschiene je 1m","ABN","12x5","Beim Lüfttemperatur 55°C",250,200,24.02235894357743]
[]
["Sammelschiene je 1m","ABN","20x5","Beim Lüfttemperatur 55°C",160,128,5.5333198789101923,288,19.5,null,null,"20x5",128,200,288,288]
["Sammelschiene je 1m","ABN","20x5","Beim Lüfttemperatur 55°C",250,200,14.014523569266254]
["Sammelschiene je 1m","ABN","20x5","Beim Lüfttemperatur 55°C",400,"288*",37.641631829321035]
[]
["Sammelschiene je 1m","ABN","12x10","Beim Lüfttemperatur 55°C",160,128,4.5766530612244898,345,23.3,null,null,"12x10",128,200,320]
["Sammelschiene je 1m","ABN","12x10","Beim Lüfttemperatur 55°C",250,200,11.403061224489797]
["Sammelschiene je 1m","ABN","12x10","Beim Lüfttemperatur 55°C",400,320,31.053061224489795]
[]
["Sammelschiene je 1m","ABN","30x5","Beim Lüfttemperatur 55°C",125,100,2.2142407718120807,399,25.2,null,null,"30x5",100,128,200,320,400]
["Sammelschiene je 1m","ABN","30x5","Beim Lüfttemperatur 55°C",160,128,3.6278120805369123]
["Sammelschiene je 1m","ABN","30x5","Beim Lüfttemperatur 55°C",250,200,9.1038470757430492]
["Sammelschiene je 1m","ABN","30x5","Beim Lüfttemperatur 55°C",400,320,24.411888782358581]
["Sammelschiene je 1m","ABN","30x5","Beim Lüfttemperatur 55°C",500,400,39.50143815915628]
[]
["Sammelschiene je 1m","ABN","20x10","Beim Lüfttemperatur 55°C",250,200,6.7702351040918884,450,24,null,null,"20x10",200,320,400]
["Sammelschiene je 1m","ABN","20x10","Beim Lüfttemperatur 55°C",400,320,17.982483847810482]
["Sammelschiene je 1m","ABN","20x10","Beim Lüfttemperatur 55°C",500,400,29.021895190236897]
[null,null,null,"Beim Lüfttemperatur 55°C"]
["Sammelschiene je 1m","ABN","30x10","Beim Lüfttemperatur 55°C",250,200,4.5464046822742477,603,29.2,null,null,"30x10",200,320,400,504]
["Sammelschiene je 1m","ABN","30x10","Beim Lüfttemperatur 55°C",400,320,11.919732441471572]
["Sammelschiene je 1m","ABN","30x10","Beim Lüfttemperatur 55°C",500,400,19.000836120401338]
["Sammelschiene je 1m","ABN","30x10","Beim Lüfttemperatur 55°C",630,504,30.962182274247489]
[]
["Sammelschiene je 1m","ABN","40x10","Beim Lüfttemperatur 55°C",400,320,8.9798782670963124,753,34.799999999999997,null,null,"40x10",320,400,504,640]
["Sammelschiene je 1m","ABN","40x10","Beim Lüfttemperatur 55°C",500,400,14.222610096670246]
["Sammelschiene je 1m","ABN","40x10","Beim Lüfttemperatur 55°C",630,504,23.035973684210525]
["Sammelschiene je 1m","ABN","40x10","Beim Lüfttemperatur 55°C",800,640,38.248764769065524]
[]
["Sammelschiene je 1m","ABN","50x10","Beim Lüfttemperatur 55°C",630,504,18.284897795591181,897,39.799999999999997,null,null,"50x10",504,640,800]
["Sammelschiene je 1m","ABN","50x10","Beim Lüfttemperatur 55°C",800,640,30.07798454050959]
["Sammelschiene je 1m","ABN","50x10","Beim Lüfttemperatur 55°C",1000,800,48.388204981391354]
[null,null,null,"Beim Lüfttemperatur 55°C"]
["Sammelschiene je 1m","ABN","60x10","Beim Lüfttemperatur 55°C",800,640,25.18483186262819,1037,45.1,null,null,"60x10",640,800,1000]
["Sammelschiene je 1m","ABN","60x10","Beim Lüfttemperatur 55°C",1000,800,40.138325781063678]
["Sammelschiene je 1m","ABN","60x10","Beim Lüfttemperatur 55°C",1250,1000,65.175590269496794]
[]
["Sammelschiene je 1m","ABN","80x10","Beim Lüfttemperatur 55°C",800,640,19.007759699624525,1306,55.1,null,null,"80x10",640,800,1000,1280]
["Sammelschiene je 1m","ABN","80x10","Beim Lüfttemperatur 55°C",1000,800,30.103701054890042]
["Sammelschiene je 1m","ABN","80x10","Beim Lüfttemperatur 55°C",1250,1000,48.141929644198093]
["Sammelschiene je 1m","ABN","80x10","Beim Lüfttemperatur 55°C",1600,1280,81.461827284105127]
[]
["Sammelschiene je 1m","ABN","100x10","Beim Lüfttemperatur 55°C",1000,800,24.761904761904763,1570,66,null,null,"100x10",800,1000,1280]
["Sammelschiene je 1m","ABN","100x10","Beim Lüfttemperatur 55°C",1250,1000,39.474742599742598]
["Sammelschiene je 1m","ABN","100x10","Beim Lüfttemperatur 55°C",1600,1280,66.388674388674389]
[]
["Sammelschiene je 1m","ABN","120x10","Beim Lüfttemperatur 55°C",1250,1000,32.318638392857146,1832,74.8,null,null,"120x10",1000,1280,1600]
["Sammelschiene je 1m","ABN","120x10","Beim Lüfttemperatur 55°C",1600,1280,54.198857142857136]
["Sammelschiene je 1m","ABN","120x10","Beim Lüfttemperatur 55°C",2000,1600,86.914285714285711]
[]
["* - Thermisches Maximum des Stroms bei einer Lufttemperatur von 55°C und einer maximalen Kupfertemperatur von 90°C"]

{"sheet":"Tabelle 4 - Pv_Sammelschiene1","index":4,"n_rows":515,"n_cols":7,"rows_kept":515,"cut":false,"hidden":false,"merged":[]}
["Art.Nr","Beschreibung","Breite","Tiefe","Querschnitt","Länge","Pol Menge, Stk"]
["XCU17C","Cu-Schiene 30X5mm für B46-S81 Z-Form lang",30,5,"30x5",160,1]
["E-CU3005150","Kupferschiene 30x5x150 aus Kupfer 30x5, 6 Bohrungen",30,5,"30x5",150,1]
["XCU17A","Cu-Schiene 30X5mm für ZW29-X68",30,5,"30x5",318,1]
["XCU17B","Cu-Schiene 30X5mm für B46-S81 Z-Form kurz",30,5,"30x5",90,1]
["MTSC12515","Sammelschiene Modul tief FB1 RE2 40mm CU 12x5mm 5p EBM 70mm",12,5,"12x5",245,3]
["MTSC23645","Sammelschiene Modul tief FB2 RE3 60mm CU 30x5mm 5p EBM 32mm",30,5,"30x5",495,3]
["XCGW182B2","CU-Sammelschienensatz 80x10mm 3p 1600A gelocht 580x100mm waagrecht FB2 für 1600A L3,N",80,10,"80x10",580,1]
["XCUW184B1","CU-SaS ungelocht 100x10x1080mm 1p 1600A",100,10,"100x10",1080,1]
["XWL910250N","Wandlerlasche CU/Sachsen 100x10x250mm für 1600A (3 Stk.)",100,10,"100x10",250,3]
["XLSSAV23L","Kupferlasche links",30,5,"30x5",307,1]
["XLSSAV23M","Kupferlasche mitte",30,5,"30x5",242,1]
["MTSC23615","Sammelschiene Modul tief FB2 RE3 60mm CU 12x5mm 5p EBM 32mm",12,5,"12x5",495,3]
["XLSSAV23R","Kupferlasche rechts",30,5,"30x5",307,1]
["XCUW182B1","CU-SaS ungelocht 100x10x580mm 1p 1600A",100,10,"100x10",580,1]
["ABNPC25132","Kupferschiene 30x10 Schrank Gr. 0 ",12,5,"12x5",495,3]
["XCUW512E","CU-Schiene FB2 12x5x540mm waagrecht einseitig um 45mm verlängert",12,5,"12x5",540,1]
["XCUW514","CU-Schiene FB4 12x5x995mm waagrecht ohne Überstand",12,5,"12x5",995,1]
["XWL310170N","Wandlerlasche CU vernickelt 30x10x170mm ohne Befestigungsschrauben (3 Stk.)",30,10,"30x10",170,3]
["XAS991C","CU-Sammelschiene 80x10mm 1p 1600A gebogen 482x187mm gelocht mit Montagezubehör",80,10,"80x10",626,1]
["XAS991D","CU-Sammelschiene 80x10mm 1p 1600A gebogen 188x138mm gelocht mit Montagezubehör",80,10,"80x10",425,1]
["XAS991SE","CU-Sammelschienensatz 80x10mm 3p 1600A Verbindung SaS zu NS-Schalter Pos. 4,5,6",80,10,"80x10",1164,1]
["XCUW522","CU-Schiene FB2 20x5x495mm waagrecht ohne Überstand",20,5,"20x5",495,1]
["XCUW111K","CU-Schiene FB1 12x10x198mm waagrecht zwischen Trägerprofil",12,10,"12x10",198,1]
["XCUW144","CU-Schiene FB4 40x10x995mm waagrecht ohne Überstand",40,10,"40x10",995,1]
["MTSC42535","Sammelschiene Modul tief FB4 RE2 40mm 2x CU 12x5mm 5p EBM 70mm",12,10,"12x10",995,3]
["XCUW134","CU-Schiene FB4 30x10x995mm waagrecht ohne Überstand",30,10,"30x10",995,1]
["MTSC22535","Sammelschiene Modul tief FB2 RE2 40mm 2x CU 12x5mm 5p EBM 70mm",12,10,"12x10",495,3]
["MTSC22643","Sammelschiene Modul tief FB2 RE2 60mm CU 30x5mm 3p EBM 32mm",30,5,"30x5",495,3]
["MTSC23735","Sammelschiene Modul tief FB2 RE3 60mm CU 12x10mm 5p EBM 70mm",12,10,"12x10",495,3]
["XCUW111","CU-Schiene FB1 12x10x245mm waagrecht ohne Überstand",12,10,"12x10",245,0]
["XCUW144B","CU-Schiene FB4 40x10x1087mm waagrecht beidseitig um 46mm verlängert",40,10,"40x10",1087,1]
["XCUW512B","CU-Schiene FB2 12x5x585mm waagrecht beidseitig um 45mm verlängert",12,5,"12x5",585,1]
["XAS991A","CU-Sammelschiene 80x10mm 1p 1600A gebogen 170x187mm gelocht mit Montagezubehör",80,10,"80x10",406,1]
["XAS991B","CU-Sammelschiene 80x10mm 1p 1600A gebogen 615x187mm gelocht mit Montagezubehör",80,10,"80x10",719,1]
["XAS991E","CU-Sammelschiene 80x10mm 1p 1600A gebogen 188x500mm gelocht mit Montagezubehör",80,10,"80x10",547,1]
["XAS991SE1","CU-Sammelschienensatz 80x10mm 3p 1600A Verbindung SaS zu NS-Schalter Pos. 1,2,3",80,10,"80x10",1646,1]
["XAS991SE2","CU-Sammelschienensatz 80x10mm 3p 1600A Verbindung SaS zu NS-Schalter Pos. 1",80,10,"80x10",1200,1]
["XCGW182B1","CU-Sammelschienensatz 100x10mm 1p 1600A gelocht 580x100mm waagrecht FB2 für 1600A L1,L2",100,10,"100x10",580,1]
["XCGW182WE3","CU-Sammelschienensatz 80x10mm 3p 1600A agewinkelt 584x10mm für Versatz auf 2. Ebene",80,10,"80x10",2190,1]
["XCUW183B1","CU-SaS ungelocht 100x10x830mm 1p 1600A",100,10,"100x10",830,1]
["XCUW185B1","CU-SaS ungelocht 100x10x1330mm 1p 1600A",100,10,"100x10",1330,1]
["ABNPC25133","Kupferschiene 30x10 Schrank Gr. 1",30,10,"30x10",686,1]
["ABNPC25134","Kupferschiene 30x10 Schrank Gr. 2",30,10,"30x10",1016,1]
["ABNPC25142","Kupferschiene 40x10 Schrank Gr. 0 ",40,10,"40x10",496,1]
["ABNPC25143","Kupferschiene 40x10 Schrank Gr. 1",40,10,"40x10",686,1]
["ABNPC25144","Kupferschiene 40x10 Schrank Gr. 2",40,10,"40x10",1016,1]
["ABNPC25532","Kupferschiene 30x5 Schrank Gr. 0 ",30,5,"30x5",496,1]
["ABNPC25533","Kupferschiene 30x5 Schrank Gr. 1",30,5,"30x5",686,1]
["ABNPC25534","Kupferschiene 30x5 Schrank Gr. 2",30,5,"30x5",1016,1]
["E-CU3005153","Kupferschiene 30x5x153 aus Kupfer 30x5, 2 x Loch 11",30,5,"30x5",153,1]
["E-CU3005178","Kupferschiene 30x5x170 aus Kupfer 30x5, versch. Löch",30,5,"30x5",170,1]
["ABNPC30131","CU-Schiene FB1 30x10mm waagrecht, gelocht für Wandlerbaustein 1-fach",30,10,"30x10",218,1]
["ABNPC30132","CU-Schiene FB2 30x10mm waagrecht, gelocht für Wandlerbaustein 1-fach",30,10,"30x10",388,1]
["ABNPC30133","CU-Schiene FB3 30x10mm waagrecht, gelocht für Wandlerbaustein 1-fach",30,10,"30x10",638,1]
["ABNPC30134","CU-Schiene FB4 30x10mm waagrecht, gelocht für Wandlerbaustein 1-fach",30,10,"30x10",888,1]
["ABNPC30135","CU-Schiene FB5 30x10mm waagrecht, gelocht für Wandlerbaustein 1-fach",30,10,"30x10",1138,1]
["ABNPC30141","CU-Schiene FB1 40x10mm waagrecht, gelocht für Wandlerbaustein 1-fach",40,10,"40x10",218,1]
["ABNPC30142","CU-Schiene FB2 40x10mm waagrecht, gelocht für Wandlerbaustein 1-fach",40,10,"40x10",388,1]
["ABNPC30143","CU-Schiene FB3 40x10mm waagrecht, gelocht für Wandlerbaustein 1-fach",40,10,"40x10",638,1]
["ABNPC30144","CU-Schiene FB4 40x10mm waagrecht, gelocht für Wandlerbaustein 1-fach",40,10,"40x10",888,1]
["ABNPC30145","CU-Schiene FB5 40x10mm waagrecht, gelocht für Wandlerbaustein 1-fach",40,10,"40x10",1138,1]
["ABNPC30531","CU-Schiene FB1 30x5mm waagrecht, gelocht für Wandlerbaustein 1-fach",30,5,"30x5",218,1]
["ABNPC30532","CU-Schiene FB2 30x5mm waagrecht, gelocht für Wandlerbaustein 1-fach",30,5,"30x5",388,1]
["ABNPC30533","CU-Schiene FB3 30x5mm waagrecht, gelocht für Wandlerbaustein 1-fach",30,5,"30x5",638,1]
["ABNPC30534","CU-Schiene FB4 30x5mm waagrecht, gelocht für Wandlerbaustein 1-fach",30,5,"30x5",888,1]
["ABNPC30535","CU-Schiene FB5 30x5mm waagrecht, gelocht für Wandlerbaustein 1-fach",30,5,"30x5",1138,1]
["ABNPC30541","CU-Schiene FB1 40x5mm waagrecht, gelocht für Wandlerbaustein 1-fach",40,5,"40x5",218,1]
["ABNPC30542","CU-Schiene FB2 40x5mm waagrecht, gelocht für Wandlerbaustein 1-fach",40,5,"40x5",388,1]
["ABNPC30543","CU-Schiene FB3 40x5mm waagrecht, gelocht für Wandlerbaustein 1-fach",40,5,"40x5",638,1]
["ABNPC30544","CU-Schiene FB4 40x5mm waagrecht, gelocht für Wandlerbaustein 1-fach",40,5,"40x5",888,1]
["ABNPC30545","CU-Schiene FB5 40x5mm waagrecht, gelocht für Wandlerbaustein 1-fach",40,5,"40x5",1138,1]
["ABNPC31141","CU-Schiene FB1 40x10mm waagrecht, gelocht einseitig verlängert für Wandlerbaustein 1-fach",40,10,"40x10",218,1]
["ABNPC31142","CU-Schiene FB2 40x10mm waagrecht, gelocht einseitig verlängert für Wandlerbaustein 1-fach",40,10,"40x10",388,1]
["ABNPC31143","CU-Schiene FB3 40x10mm waagrecht, gelocht einseitig verlängert für Wandlerbaustein 1-fach",40,10,"40x10",638,1]
["ABNPC31144","CU-Schiene FB4 40x10mm waagrecht, gelocht einseitig verlängert für Wandlerbaustein 1-fach",40,10,"40x10",888,1]
["ABNPC31145","CU-Schiene FB5 40x10mm waagrecht, gelocht einseitig verlängert für Wandlerbaustein 1-fach",40,10,"40x10",1138,1]
["ABNPC31541","CU-Schiene FB1 40x5mm waagrecht, gelocht einseitig verlängert für Wandlerbaustein 1-fach",40,5,"40x5",218,1]
["ABNPC31542","CU-Schiene FB2 40x5mm waagrecht, gelocht einseitig verlängert für Wandlerbaustein 1-fach",40,5,"40x5",388,1]
["ABNPC31543","CU-Schiene FB3 40x5mm waagrecht, gelocht einseitig verlängert für Wandlerbaustein 1-fach",40,5,"40x5",638,1]
["ABNPC31544","CU-Schiene FB4 40x5mm waagrecht, gelocht einseitig verlängert für Wandlerbaustein 1-fach",40,5,"40x5",888,1]
["ABNPC31545","CU-Schiene FB5 40x5mm waagrecht, gelocht einseitig verlängert für Wandlerbaustein 1-fach",40,5,"40x5",1138,1]
["ABNPC32141","CU-Schiene FB1 40x10mm waagrecht, gelocht beidseitig verlängert für Wandlerbaustein 1-fach",40,10,"40x10",218,1]
["ABNPC32142","CU-Schiene FB2 40x10mm waagrecht, gelocht beidseitig verlängert für Wandlerbaustein 1-fach",40,10,"40x10",388,1]
["ABNPC32143","CU-Schiene FB3 40x10mm waagrecht, gelocht beidseitig verlängert für Wandlerbaustein 1-fach",40,10,"40x10",638,1]
["ABNPC32144","CU-Schiene FB4 40x10mm waagrecht, gelocht beidseitig verlängert für Wandlerbaustein 1-fach",40,10,"40x10",888,1]
["ABNPC32145","CU-Schiene FB5 40x10mm waagrecht, gelocht beidseitig verlängert für Wandlerbaustein 1-fach",40,10,"40x10",1138,1]
["ABNPC32541","CU-Schiene FB1 40x5mm waagrecht, gelocht beidseitig verlängert für Wandlerbaustein 1-fach",40,5,"40x5",218,1]
["ABNPC32542","CU-Schiene FB2 40x5mm waagrecht, gelocht beidseitig verlängert für Wandlerbaustein 1-fach",40,5,"40x5",388,1]
["ABNPC32543","CU-Schiene FB3 40x5mm waagrecht, gelocht beidseitig verlängert für Wandlerbaustein 1-fach",40,5,"40x5",638,1]
["ABNPC32544","CU-Schiene FB4 40x5mm waagrecht, gelocht beidseitig verlängert für Wandlerbaustein 1-fach",40,5,"40x5",888,1]
["ABNPC32545","CU-Schiene FB5 40x5mm waagrecht, gelocht beidseitig verlängert für Wandlerbaustein 1-fach",40,5,"40x5",1138,1]
["ABNPC33130","CU-Schiene FB0,5 30x10mm waagrecht, gelocht für Wandlerlasche",30,10,"30x10",188,1]
["ABNPC33141","CU-Schiene FB1 40x10mm waagrecht, gelocht, links  für Wandlerlasche",40,10,"40x10",263,1]
["ABNPC33142","CU-Schiene FB2 40x10mm waagrecht, gelocht, links  für Wandlerlasche",40,10,"40x10",513,1]
["ABNPC33143","CU-Schiene FB3 40x10mm waagrecht, gelocht, links  für Wandlerlasche",40,10,"40x10",763,1]
["ABNPC34141","CU-Schiene FB1 40x10mm waagrecht, gelocht, rechts  für Wandlerlasche",40,10,"40x10",283,1]
["ABNPC34142","CU-Schiene FB2 40x10mm waagrecht, gelocht, rechts  für Wandlerlasche",40,10,"40x10",533,1]
["ABNPC34143","CU-Schiene FB3 40x10mm waagrecht, gelocht, rechts  für Wandlerlasche",40,10,"40x10",783,1]
["ABNPC35141","CU-Schiene FB1 40x10mm waagrecht, gelocht, links  einseitig verlängert für Wandlerlasche",40,10,"40x10",322,1]
["ABNPC35142","CU-Schiene FB2 40x10mm waagrecht, gelocht, links  einseitig verlängert für Wandlerlasche",40,10,"40x10",596,1]
["ABNPC35143","CU-Schiene FB3 40x10mm waagrecht, gelocht, links  einseitig verlängert für Wandlerlasche",40,10,"40x10",862,1]
["ABNPC36141","CU-Schiene FB1 40x10mm waagrecht, gelocht, rechts  einseitig verlängert für Wandlerlasche",40,10,"40x10",342,1]
["ABNPC36142","CU-Schiene FB2 40x10mm waagrecht, gelocht, rechts  einseitig verlängert für Wandlerlasche",40,10,"40x10",592,1]
["ABNPC36143","CU-Schiene FB3 40x10mm waagrecht, gelocht, rechts  einseitig verlängert für Wandlerlasche",40,10,"40x10",842,1]
["MFSC12613","Sammelschiene Modul flach FB1 RE2 60mm CU 12x5mm 3p EBM 32mm",12,5,"12x5",245,3]
["MFSC12633","Sammelschiene Modul flach FB1 RE2 60mm CU 12x10mm 3p EBM 32mm",12,10,"12x10",245,3]
["MFSC12643","Sammelschiene Modul flach FB1 RE2 60mm CU 30x5mm 3p EBM 32mm",3,5,"3x5",245,3]
["MFSC13615","Sammelschiene Modul flach FB1 RE3 60mm CU 12x5mm 5p EBM 32mm",12,5,"12x5",245,3]
["MFSC13625","Sammelschiene Modul flach FB1 RE3 60mm CU 20x5mm 5p EBM 32mm",20,5,"20x5",245,3]
["MFSC13635","Sammelschiene Modul flach FB1 RE3 60mm CU 12x10mm 5p EBM 32mm",12,10,"12x10",245,3]
["MFSC13645","Sammelschiene Modul flach FB1 RE3 60mm CU 30x5mm 5p EBM 32mm",30,5,"30x5",245,3]
["MFSC15963","Sammelschiene Modul flach FB1 RE5 185mm CU 30x10mm 3p EBM 150mm",30,10,"30x10",245,3]
["MFSC15983","Sammelschiene Modul flach FB1 RE5 185mm CU 50x10mm 3p EBM 150mm",50,10,"50x10",245,3]
["MFSC17965","Sammelschiene Modul flach FB1 RE7 185mm CU 30x10mm 5p EBM 150mm",30,10,"30x10",245,3]
["MFSC18985","Sammelschiene Modul flach FB1 RE8 185mm CU 50x10mm 5p EBM 150mm",50,10,"50x10",245,3]
["MFSC22613","Sammelschiene Modul flach FB2 RE2 60mm CU 12x5mm 3p EBM 32mm",12,5,"12x5",495,3]
["MFSC22633","Sammelschiene Modul flach FB2 RE2 60mm CU 12x10mm 3p EBM 32mm",12,10,"12x10",495,3]
["MFSC22643","Sammelschiene Modul flach FB2 RE2 60mm CU 30x5mm 3p EBM 32mm",30,5,"30x5",495,3]
["MFSC23615","Sammelschiene Modul flach FB2 RE3 60mm CU 12x5mm 5p EBM 32mm",12,5,"12x5",495,3]
["MFSC23635","Sammelschiene Modul flach FB2 RE3 60mm CU 12x10mm 5p EBM 32mm",12,10,"12x10",495,3]
["MFSC23645","Sammelschiene Modul flach FB2 RE3 60mm CU 30x5mm 5p EBM 32mm",30,5,"30x5",495,3]
["MFSC25963","Sammelschiene Modul flach FB2 RE5 185mm CU 30x10mm 3p EBM 150mm",30,10,"30x10",495,3]
["MFSC25983","Sammelschiene Modul flach FB2 RE5 185mm CU 50x10mm 3p EBM 150mm",50,10,"50x10",495,3]
["MFSC27965","Sammelschiene Modul flach FB2 RE7 185mm CU 30x10mm 5p EBM 150mm",30,10,"30x10",495,3]
["MFSC28985","Sammelschiene Modul flach FB2 RE8 185mm CU 50x10mm 5p EBM 150mm",50,10,"50x10",495,3]
["MFSC32613","Sammelschiene Modul flach FB3 RE2 60mm CU 12x5mm 3p EBM 32mm",12,5,"12x5",745,3]
["MFSC32633","Sammelschiene Modul flach FB3 RE2 60mm CU 12x10mm 3p EBM 32mm",12,10,"12x10",745,3]
["MFSC32643","Sammelschiene Modul flach FB3 RE2 60mm CU 30x5mm 3p EBM 32mm",30,5,"30x5",745,3]
["MFSC33615","Sammelschiene Modul flach FB3 RE3 60mm CU 12x5mm 5p EBM 32mm",12,5,"12x5",745,3]
["MFSC33635","Sammelschiene Modul flach FB3 RE3 60mm CU 12x10mm 5p EBM 32mm",12,10,"12x10",745,3]
["MFSC33645","Sammelschiene Modul flach FB3 RE3 60mm CU 30x5mm 5p EBM 32mm",30,5,"30x5",745,3]
["MFSC35963","Sammelschiene Modul flach FB3 RE5 185mm CU 30x10mm 3p EBM 150mm",30,10,"30x10",745,3]
["MFSC35983","Sammelschiene Modul flach FB3 RE5 185mm CU 50x10mm 3p EBM 150mm",50,10,"50x10",745,3]
["MFSC37965","Sammelschiene Modul flach FB3 RE7 185mm CU 30x10mm 5p EBM 150mm",30,10,"30x10",745,3]
["MFSC38985","Sammelschiene Modul flach FB3 RE8 185mm CU 50x10mm 5p EBM 150mm",50,10,"50x10",745,3]
["MFSC42613","Sammelschiene Modul flach FB4 RE2 60mm CU 12x5mm 3p EBM 32mm",12,5,"12x5",995,3]
["MFSC42633","Sammelschiene Modul flach FB4 RE2 60mm CU 12x10mm 3p EBM 32mm",12,10,"12x10",995,3]
["MFSC42643","Sammelschiene Modul flach FB4 RE2 60mm CU 30x5mm 3p EBM 32mm",30,5,"30x5",995,3]
["MFSC43615","Sammelschiene Modul flach FB4 RE3 60mm CU 12x5mm 5p EBM 32mm",12,5,"12x5",995,3]
["MFSC43635","Sammelschiene Modul flach FB4 RE3 60mm CU 12x10mm 5p EBM 32mm",12,10,"12x10",995,3]
["MFSC43645","Sammelschiene Modul flach FB4 RE3 60mm CU 30x5mm 5p EBM 32mm",30,5,"30x5",995,3]
["MFSC45963","Sammelschiene Modul flach FB4 RE5 185mm CU 30x10mm 3p EBM 150mm",30,10,"30x10",995,3]
["MFSC45983","Sammelschiene Modul flach FB4 RE5 185mm CU 50x10mm 3p EBM 150mm",50,10,"50x10",995,3]
["MFSC47965","Sammelschiene Modul flach FB4 RE7 185mm CU 30x10mm 5p EBM 150mm",30,10,"30x10",995,3]
["MFSC48985","Sammelschiene Modul flach FB4 RE8 185mm CU 50x10mm 5p EBM 150mm",50,10,"50x10",995,3]
["MFSC52613","Sammelschiene Modul flach FB5 RE2 60mm CU 12x5mm 3p EBM 32mm",12,5,"12x5",1245,3]
["MFSC52633","Sammelschiene Modul flach FB5 RE2 60mm CU 12x10mm 3p EBM 32mm",12,10,"12x10",1245,3]
["MFSC52643","Sammelschiene Modul flach FB5 RE2 60mm CU 30x5mm 3p EBM 32mm",30,5,"30x5",1245,3]
["MFSC53615","Sammelschiene Modul flach FB5 RE3 60mm CU 12x5mm 5p EBM 32mm",12,5,"12x5",1245,3]
["MFSC53635","Sammelschiene Modul flach FB5 RE3 60mm CU 12x10mm 5p EBM 32mm",12,10,"12x10",1245,3]
["MFSC53645","Sammelschiene Modul flach FB5 RE3 60mm CU 30x5mm 5p EBM 32mm",30,5,"30x5",1245,3]
["MFSC55963","Sammelschiene Modul flach FB5 RE5 185mm CU 30x10mm 3p EBM 150mm",30,10,"30x10",1245,3]
["MFSC55983","Sammelschiene Modul flach FB5 RE5 185mm CU 50x10mm 3p EBM 150mm",50,10,"50x10",1245,3]
["MFSC57965","Sammelschiene Modul flach FB5 RE7 185mm CU 30x10mm 5p EBM 150mm",30,10,"30x10",1245,3]
["MFSC58985","Sammelschiene Modul flach FB5 RE8 185mm CU 50x10mm 5p EBM 150mm",50,10,"50x10",1245,3]
["MTSC12535","Sammelschiene Modul tief FB1 RE2 40mm 2x CU 12x5mm 5p EBM 70mm",12,5,"12x5",245,3]
["MTSC12613","Sammelschiene Modul tief FB1 RE2 60mm CU 12x5mm 3p EBM 32mm",12,5,"12x5",245,3]
["MTSC12633","Sammelschiene Modul tief FB1 RE2 60mm CU 12x10mm 3p EBM 32mm",12,10,"12x10",245,3]
["MTSC12643","Sammelschiene Modul tief FB1 RE2 60mm CU 30x5mm 3p EBM 32mm",30,5,"30x5",245,3]
["MTSC12733","Sammelschiene Modul tief FB1 RE2 60mm CU 12x10mm 3p EBM 70mm",12,10,"12x10",245,3]
["MTSC12743","Sammelschiene Modul tief FB1 RE2 60mm CU 30x5mm 3p EBM 70mm",30,5,"30x5",245,3]
["MTSC12763","Sammelschiene Modul tief FB1 RE2 60mm CU 30x10mm 3p EBM 70mm",30,10,"30x10",245,3]
["MTSC13615","Sammelschiene Modul tief FB1 RE3 60mm CU 12x5mm 5p EBM 32mm",12,5,"12x5",245,3]
["MTSC13635","Sammelschiene Modul tief FB1 RE3 60mm CU 12x10mm 5p EBM 32mm",12,10,"12x10",245,3]
["MTSC13645","Sammelschiene Modul tief FB1 RE3 60mm CU 30x5mm 5p EBM 32mm",30,5,"30x5",245,3]
["MTSC13735","Sammelschiene Modul tief FB1 RE3 60mm CU 12x10mm 5p EBM 70mm",12,10,"12x10",245,3]
["MTSC13745","Sammelschiene Modul tief FB1 RE3 60mm CU 30x5mm 5p EBM 70mm",30,5,"30x5",245,3]
["MTSC13765","Sammelschiene Modul tief FB1 RE3 60mm CU 30x10mm 5p EBM 70mm",30,10,"30x10",245,3]
["MTSC15963","Sammelschiene Modul tief FB1 RE5 185mm CU 30x10mm 3p EBM 150mm",30,10,"30x10",245,3]
["MTSC15983","Sammelschiene Modul tief FB1 RE5 185mm CU 50x10mm 3p EBM 150mm",50,10,"50x10",245,3]
["MTSC17965","Sammelschiene Modul tief FB1 RE7 185mm CU 30x10mm 5p EBM 150mm",30,10,"30x10",245,3]
["MTSC18985","Sammelschiene Modul tief FB1 RE8 185mm CU 50x10mm 5p EBM 150mm",50,10,"50x10",245,3]
["MTSC22515","Sammelschiene Modul tief FB2 RE2 40mm CU 12x5mm 5p EBM 70mm",12,5,"12x5",495,3]
["MTSC22613","Sammelschiene Modul tief FB2 RE2 60mm CU 12x5mm 3p EBM 32mm",12,5,"12x5",495,3]
["MTSC22633","Sammelschiene Modul tief FB2 RE2 60mm CU 12x10mm 3p EBM 32mm",12,10,"12x10",495,3]
["MTSC22653","Sammelschiene Modul tief FB2 RE2 60mm CU 20x10mm 3p EBM 32mm",20,10,"20x10",495,3]
["MTSC22733","Sammelschiene Modul tief FB2 RE2 60mm CU 12x10mm 3p EBM 70mm",12,10,"12x10",495,3]
["MTSC22743","Sammelschiene Modul tief FB2 RE2 60mm CU 30x5mm 3p EBM 70mm",30,5,"30x5",495,3]
["MTSC22763","Sammelschiene Modul tief FB2 RE2 60mm CU 30x10mm 3p EBM 70mm",30,10,"30x10",495,3]
["MTSC23635","Sammelschiene Modul tief FB2 RE3 60mm CU 12x10mm 5p EBM 32mm",12,10,"12x10",495,3]
["MTSC23745","Sammelschiene Modul tief FB2 RE3 60mm CU 30x5mm 5p EBM 70mm",30,5,"30x5",495,3]
["MTSC23765","Sammelschiene Modul tief FB2 RE3 60mm CU 30x10mm 5p EBM 70mm",30,10,"30x10",495,3]
["MTSC25963","Sammelschiene Modul tief FB2 RE5 185mm CU 30x10mm 3p EBM 150mm",30,10,"30x10",495,3]
["MTSC25983","Sammelschiene Modul tief FB2 RE5 185mm CU 50x10mm 3p EBM 150mm",50,10,"50x10",495,3]
["MTSC27965","Sammelschiene Modul tief FB2 RE7 185mm CU 30x10mm 5p EBM 150mm",30,10,"30x10",495,3]
["MTSC28985","Sammelschiene Modul tief FB2 RE8 185mm CU 50x10mm 5p EBM 150mm",50,10,"50x10",495,3]
["MTSC32515","Sammelschiene Modul tief FB3 RE2 40mm CU 12x5mm 5p EBM 70mm",12,5,"12x5",745,3]
["MTSC32535","Sammelschiene Modul tief FB3 RE2 40mm 2x CU 12x5mm 5p EBM 70mm",12,5,"12x5",745,3]
["MTSC32613","Sammelschiene Modul tief FB3 RE2 60mm CU 12x5mm 3p EBM 32mm",12,5,"12x5",745,3]
["MTSC32633","Sammelschiene Modul tief FB3 RE2 60mm CU 12x10mm 3p EBM 32mm",12,10,"12x10",745,3]
["MTSC32643","Sammelschiene Modul tief FB3 RE2 60mm CU 30x5mm 3p EBM 32mm",30,5,"30x5",745,3]
["MTSC32733","Sammelschiene Modul tief FB3 RE2 60mm CU 12x10mm 3p EBM 70mm",12,10,"12x10",745,3]
["MTSC32743","Sammelschiene Modul tief FB3 RE2 60mm CU 30x5mm 3p EBM 70mm",30,5,"30x5",745,3]
["MTSC32763","Sammelschiene Modul tief FB3 RE2 60mm CU 30x10mm 3p EBM 70mm",30,10,"30x10",745,3]
["MTSC33615","Sammelschiene Modul tief FB3 RE3 60mm CU 12x5mm 5p EBM 32mm",12,5,"12x5",745,3]
["MTSC33635","Sammelschiene Modul tief FB3 RE3 60mm CU 12x10mm 5p EBM 32mm",12,10,"12x10",745,3]
["MTSC33645","Sammelschiene Modul tief FB3 RE3 60mm CU 30x5mm 5p EBM 32mm",30,5,"30x5",745,3]
["MTSC33735","Sammelschiene Modul tief FB3 RE3 60mm CU 12x10mm 5p EBM 70mm",12,10,"12x10",745,3]
["MTSC33745","Sammelschiene Modul tief FB3 RE3 60mm CU 30x5mm 5p EBM 70mm",30,5,"30x5",745,3]
["MTSC33765","Sammelschiene Modul tief FB3 RE3 60mm CU 30x10mm 5p EBM 70mm",30,10,"30x10",745,3]
["MTSC35963","Sammelschiene Modul tief FB3 RE5 185mm CU 30x10mm 3p EBM 150mm",30,10,"30x10",745,3]
["MTSC35983","Sammelschiene Modul tief FB3 RE5 185mm CU 50x10mm 3p EBM 150mm",50,10,"50x10",745,3]
["MTSC35993","Sammelschiene Modul tief FB3 RE5 185mm CU 60x10mm 3p EBM 150mm",60,10,"60x10",745,3]
["MTSC37965","Sammelschiene Modul tief FB3 RE7 185mm CU 30x10mm 5p EBM 150mm",30,10,"30x10",745,3]
["MTSC38985","Sammelschiene Modul tief FB3 RE8 185mm CU 50x10mm 5p EBM 150mm",50,10,"50x10",745,3]
["MTSC42515","Sammelschiene Modul tief FB4 RE2 40mm CU 12x5mm 5p EBM 70mm",12,5,"12x5",995,3]
["MTSC42613","Sammelschiene Modul tief FB4 RE2 60mm CU 12x5mm 3p EBM 32mm",12,5,"12x5",995,3]
["MTSC42633","Sammelschiene Modul tief FB4 RE2 60mm CU 12x10mm 3p EBM 32mm",12,10,"12x10",995,3]
["MTSC42643","Sammelschiene Modul tief FB4 RE2 60mm CU 30x5mm 3p EBM 32mm",30,5,"30x5",995,3]
["MTSC42733","Sammelschiene Modul tief FB4 RE2 60mm CU 12x10mm 3p EBM 70mm",12,10,"12x10",995,3]
["MTSC42743","Sammelschiene Modul tief FB4 RE2 60mm CU 30x5mm 3p EBM 70mm",30,5,"30x5",995,3]
["MTSC42753","Sammelschiene Modul tief FB4 RE2 60mm CU 20x10mm 3p EBM 70mm",20,10,"20x10",995,3]
["MTSC42763","Sammelschiene Modul tief FB4 RE2 60mm CU 30x10mm 3p EBM 70mm",30,10,"30x10",995,3]
["MTSC43615","Sammelschiene Modul tief FB4 RE3 60mm CU 12x5mm 5p EBM 32mm",12,5,"12x5",995,3]
["MTSC43635","Sammelschiene Modul tief FB4 RE3 60mm CU 12x10mm 5p EBM 32mm",12,10,"12x10",995,3]
["MTSC43645","Sammelschiene Modul tief FB4 RE3 60mm CU 30x5mm 5p EBM 32mm",30,5,"30x5",995,3]
["MTSC43735","Sammelschiene Modul tief FB4 RE3 60mm CU 12x10mm 5p EBM 70mm",12,10,"12x10",995,3]
["MTSC43745","Sammelschiene Modul tief FB4 RE3 60mm CU 30x5mm 5p EBM 70mm",30,5,"30x5",995,3]
["MTSC43765","Sammelschiene Modul tief FB4 RE3 60mm CU 30x10mm 5p EBM 70mm",30,10,"30x10",995,3]
["MTSC45963","Sammelschiene Modul tief FB4 RE5 185mm CU 30x10mm 3p EBM 150mm",30,10,"30x10",995,3]
["MTSC45973","Sammelschiene Modul tief FB4 RE5 185mm CU 40x10mm 3p EBM 150mm",40,10,"40x10",995,3]
["MTSC45983","Sammelschiene Modul tief FB4 RE5 185mm CU 50x10mm 3p EBM 150mm",50,10,"50x10",995,3]
["MTSC47965","Sammelschiene Modul tief FB4 RE7 185mm CU 30x10mm 5p EBM 150mm",30,10,"30x10",995,3]
["MTSC48985","Sammelschiene Modul tief FB4 RE8 185mm CU 50x10mm 5p EBM 150mm",50,10,"50x10",995,3]
["MTSC52515","Sammelschiene Modul tief FB5 RE2 40mm CU 12x5mm 5p EBM 70mm",12,5,"12x5",1245,3]
["MTSC52535","Sammelschiene Modul tief FB5 RE2 40mm 2x CU 12x5mm 5p EBM 70mm",12,5,"12x5",1245,3]
["MTSC52613","Sammelschiene Modul tief FB5 RE2 60mm CU 12x5mm 3p EBM 32mm",12,5,"12x5",1245,3]
["MTSC52633","Sammelschiene Modul tief FB5 RE2 60mm CU 12x10mm 3p EBM 32mm",12,10,"12x10",1245,3]
["MTSC52643","Sammelschiene Modul tief FB5 RE2 60mm CU 30x5mm 3p EBM 32mm",30,5,"30x5",1245,3]
["MTSC52733","Sammelschiene Modul tief FB5 RE2 60mm CU 12x10mm 3p EBM 70mm",12,10,"12x10",1245,3]
["MTSC52743","Sammelschiene Modul tief FB5 RE2 60mm CU 30x5mm 3p EBM 70mm",30,5,"30x5",1245,3]
["MTSC52763","Sammelschiene Modul tief FB5 RE2 60mm CU 30x10mm 3p EBM 70mm",30,10,"30x10",1245,3]
["MTSC53615","Sammelschiene Modul tief FB5 RE3 60mm CU 12x5mm 5p EBM 32mm",12,5,"12x5",1245,3]
["MTSC53635","Sammelschiene Modul tief FB5 RE3 60mm CU 12x10mm 5p EBM 32mm",12,10,"12x10",1245,3]
["MTSC53645","Sammelschiene Modul tief FB5 RE3 60mm CU 30x5mm 5p EBM 32mm",30,5,"30x5",1245,3]
["MTSC53735","Sammelschiene Modul tief FB5 RE3 60mm CU 12x10mm 5p EBM 70mm",12,10,"12x10",1245,3]
["MTSC53745","Sammelschiene Modul tief FB5 RE3 60mm CU 30x5mm 5p EBM 70mm",30,5,"30x5",1245,3]
["MTSC53765","Sammelschiene Modul tief FB5 RE3 60mm CU 30x10mm 5p EBM 70mm",30,10,"30x10",1245,3]
["MTSC55963","Sammelschiene Modul tief FB5 RE5 185mm CU 30x10mm 3p EBM 150mm",30,10,"30x10",1245,3]
["MTSC55983","Sammelschiene Modul tief FB5 RE5 185mm CU 50x10mm 3p EBM 150mm",50,10,"50x10",1245,3]
["MTSC57965","Sammelschiene Modul tief FB5 RE7 185mm CU 30x10mm 5p EBM 150mm",30,10,"30x10",1245,3]
["MTSC58985","Sammelschiene Modul tief FB5 RE8 185mm CU 50x10mm 5p EBM 150mm",50,10,"50x10",1245,3]
["MXSC11211","Sammelschiene Modul tief FB1 RE1 CU 12x5mm z.Tr.1p N/PE",12,5,"12x5",245,3]
["MXSC11231","Sammelschiene Modul tief FB1 RE1 CU 12x10mm z.Tr.1p N/PE",12,10,"12x10",245,3]
["MXSC11311","Sammelschiene Modul FB1 RE1 CU 12x5mm 27° hinter dem Traggerüst 1p N/PE",12,5,"12x5",245,3]
["MXSC11331","Sammelschiene Modul FB1 RE1 CU 12x10mm 27° hinter dem Traggerüst 1p N/PE",12,10,"12x10",245,3]
["MXSC11341","Sammelschiene Modul FB1 RE1 CU 30x5mm 27° hinter dem Traggerüst 1p N/PE",30,5,"30x5",245,3]
["MXSC11361","Sammelschiene Modul FB1 RE1 CU 30x10mm 27° hinter dem Traggerüst 1p N/PE",30,10,"30x10",245,3]
["MXSC11411","Sammelschiene Modul FB1 RE1 CU 12x5mm 30° Standard 1p N/PE",12,5,"12x5",245,3]
["MXSC11431","Sammelschiene Modul FB1 RE1 CU 12x10mm 30° vor dem dem Traggerüst 1p N/PE",12,10,"12x10",245,3]
["MXSC11441","Sammelschiene Modul FB1 RE1 CU 30x5mm 30° Standard 1p N/PE",30,5,"30x5",245,3]
["MXSC11461","Sammelschiene Modul FB1 RE1 CU 30x10mm 30° Standard 1p N/PE",30,10,"30x10",245,3]
["MXSC21211","Sammelschiene Modul tief FB2 RE1 CU 12x5mm z.Tr.1p N/PE",12,5,"12x5",495,3]
["MXSC21231","Sammelschiene Modul tief FB2 RE1 CU 12x10mm z.Tr.1p N/PE",12,10,"12x10",495,3]
["MXSC21311","Sammelschiene Modul FB2 RE1 CU 12x5mm 27° hinter dem Traggerüst 1p N/PE",12,5,"12x5",495,3]
["MXSC21331","Sammelschiene Modul FB2 RE1 CU 12x10mm 27° hinter dem Traggerüst 1p N/PE",12,10,"12x10",495,3]
["MXSC21341","Sammelschiene Modul FB2 RE1 CU 30x5mm 27° hinter dem Traggerüst 1p N/PE",30,5,"30x5",495,3]
["MXSC21361","Sammelschiene Modul FB2 RE1 CU 30x10mm 27° hinter dem Traggerüst 1p N/PE",30,10,"30x10",495,3]
["MXSC21411","Sammelschiene Modul FB2 RE1 CU 12x5mm 30° Standard 1p N/PE",12,5,"12x5",495,3]
["MXSC21431","Sammelschiene Modul FB2 RE1 CU 12x10mm 30° Standard 1p N/PE",12,10,"12x10",495,3]
["MXSC21441","Sammelschiene Modul FB2 RE1 CU 30x5mm 30° Standard 1p N/PE",30,5,"30x5",495,3]
["MXSC21461","Sammelschiene Modul FB2 RE1 CU 30x10mm 30° Standard 1p N/PE",30,10,"30x10",495,3]
["MXSC31311","Sammelschiene Modul FB3 RE1 CU 12x5mm 27° hinter dem Traggerüst 1p N/PE",12,5,"12x5",745,3]
["MXSC31331","Sammelschiene Modul FB3 RE1 CU 12x10mm 27° hinter dem Traggerüst 1p N/PE",12,10,"12x10",745,3]
["MXSC31341","Sammelschiene Modul FB3 RE1 CU 30x5mm 27° hinter dem Traggerüst 1p N/PE",30,5,"30x5",745,3]
["MXSC31351","Sammelschiene Modul FB3 RE1 CU 20x10mm 27° hinter dem Traggerüst 1p N/PE",20,10,"20x10",745,3]
["MXSC31361","Sammelschiene Modul FB3 RE1 CU 30x10mm 27° hinter dem Traggerüst 1p N/PE",30,10,"30x10",745,3]
["MXSC31411","Sammelschiene Modul FB3 RE1 CU 12x5mm 30° Standard 1p N/PE",12,5,"12x5",745,3]
["MXSC31431","Sammelschiene Modul FB3 RE1 CU 12x10mm 30° Standard 1p N/PE",12,10,"12x10",745,3]
["MXSC31441","Sammelschiene Modul FB3 RE1 CU 30x5mm 30° Standard 1p N/PE",30,5,"30x5",745,3]
["MXSC31461","Sammelschiene Modul FB3 RE1 CU 30x10mm 30° Standard 1p N/PE",30,10,"30x10",745,3]
["MXSC41311","Sammelschiene Modul FB4 RE1 CU 12x5mm 27° hinter dem Traggerüst 1p N/PE",12,5,"12x5",995,3]
["MXSC41331","Sammelschiene Modul FB4 RE1 CU 12x10mm 27° hinter dem Traggerüst 1p N/PE",12,10,"12x10",995,3]
["MXSC41341","Sammelschiene Modul FB4 RE1 CU 30x5mm 27° hinter dem Traggerüst 1p N/PE",30,5,"30x5",995,3]
["MXSC41361","Sammelschiene Modul FB4 RE1 CU 30x10mm 27° hinter dem Traggerüst 1p N/PE",30,10,"30x10",995,3]
["MXSC41411","Sammelschiene Modul FB4 RE1 CU 12x5mm 30° Standard 1p N/PE",12,5,"12x5",995,3]
["MXSC41431","Sammelschiene Modul FB4 RE1 CU 12x10mm 30° Standard 1p N/PE",12,10,"12x10",995,3]
["MXSC41441","Sammelschiene Modul FB4 RE1 CU 30x5mm 30° Standard 1p N/PE",30,5,"30x5",995,3]
["MXSC41461","Sammelschiene Modul FB4 RE1 CU 30x10mm 30° Standard 1p N/PE",30,10,"30x10",995,3]
["MXSC51311","Sammelschiene Modul FB5 RE1 CU 12x5mm 27° hinter dem Traggerüst 1p N/PE",12,5,"12x5",1245,3]
["MXSC51331","Sammelschiene Modul FB5 RE1 CU 12x10mm 27° hinter dem Traggerüst 1p N/PE",12,10,"12x10",1245,3]
["MXSC51341","Sammelschiene Modul FB5 RE1 CU 30x5mm 27° hinter dem Traggerüst 1p N/PE",30,5,"30x5",1245,3]
["MXSC51361","Sammelschiene Modul FB5 RE1 CU 30x10mm 27° hinter dem Traggerüst 1p N/PE",30,10,"30x10",1245,3]
["MXSC51411","Sammelschiene Modul FB5 RE1 CU 12x5mm 30° Standard 1p N/PE",12,5,"12x5",1245,3]
["MXSC51431","Sammelschiene Modul FB5 RE1 CU 12x10mm 30° Standard 1p N/PE",12,10,"12x10",1245,3]
["MXSC51441","Sammelschiene Modul FB5 RE1 CU 30x5mm 30° Standard 1p N/PE",30,5,"30x5",1245,3]
["MXSC51461","Sammelschiene Modul FB5 RE1 CU 30x10mm 30° Standard 1p N/PE",30,10,"30x10",1245,3]
["PB102C0551","1FB SAS 40mm 5p  CU12x5 250A",12,5,"12x5",1245,3]
["PB102C0553","1FB SAS 40mm 5p  CU 2x12x5 355A",12,10,"12x10",1245,3]
["PB202C0553","Sammelschiene Modul tief FB2 RE2 40mm 2x CU 12x5mm 5p EBM 70mm",12,10,"12x10",1245,3]
["PC22250N03","Wandlerlasche CU vernickelt 50x12x250mm",50,12,"50x12",250,1]
["XCUS112","CU-Schiene RE2 12x10x295mm senkrecht ohne Überstand",12,10,"12x10",295,1]
["XCUS113","CU-Schiene RE3 12x10x445mm senkrecht ohne Überstand",12,10,"12x10",445,1]
["XCUS114","CU-Schiene RE4 12x10x595mm senkrecht ohne Überstand",12,10,"12x10",595,1]
["XCUS115","CU-Schiene RE5 12x10x745mm senkrecht ohne Überstand",12,10,"12x10",745,1]
["XCUS122","CU-Schiene RE2 20x10x295mm senkrecht ohne Überstand",20,10,"20x10",295,1]
["XCUS123","CU-Schiene RE3 20x10x445mm senkrecht ohne Überstand",20,10,"20x10",445,1]
["XCUS124","CU-Schiene RE4 20x10x595mm senkrecht ohne Überstand",20,10,"20x10",595,1]
["XCUS125","CU-Schiene RE5 20x10x745mm senkrecht ohne Überstand",20,10,"20x10",745,1]
["XCUS132","CU-Schiene RE2 30x10x295mm senkrecht ohne Überstand",30,10,"30x10",295,1]
["XCUS133","CU-Schiene RE3 30x10x445mm senkrecht ohne Überstand",30,10,"30x10",445,1]
["XCUS134","CU-Schiene RE4 30x10x595mm senkrecht ohne Überstand",30,10,"30x10",595,1]
["XCUS135","CU-Schiene RE5 30x10x745mm senkrecht ohne Überstand",30,10,"30x10",745,1]
["XCUS512","CU-Schiene RE2 12x5x295mm senkrecht ohne Überstand",12,5,"12x5",295,1]
["XCUS513","CU-Schiene RE3 12x5x445mm senkrecht ohne Überstand",12,5,"12x5",445,1]
["XCUS514","CU-Schiene RE4 12x5x595mm senkrecht ohne Überstand",12,5,"12x5",595,1]
["XCUS515","CU-Schiene RE5 12x5x745mm senkrecht ohne Überstand",12,5,"12x5",745,1]
["XCUS522","CU-Schiene RE2 20x5x295mm senkrecht ohne Überstand",20,5,"20x5",295,1]
["XCUS523","CU-Schiene RE3 20x5x445mm senkrecht ohne Überstand",20,5,"20x5",445,1]
["XCUS524","CU-Schiene RE4 20x5x595mm senkrecht ohne Überstand",20,5,"20x5",595,1]
["XCUS525","CU-Schiene RE5 20x5x745mm senkrecht ohne Überstand",20,5,"20x5",745,1]
["XCUS532","CU-Schiene RE2 30x5x295mm senkrecht ohne Überstand",30,5,"30x5",295,1]
["XCUS533","CU-Schiene RE3 30x5x445mm senkrecht ohne Überstand",30,5,"30x5",445,1]
["XCUS534","CU-Schiene RE4 30x5x595mm senkrecht ohne Überstand",30,5,"30x5",595,1]
["XCUS535","CU-Schiene RE5 30x5x745mm senkrecht ohne Überstand",30,5,"30x5",745,1]
["XCUW111B","CU-Schiene FB1 12x10x335mm waagrecht beidseitig um 45mm verlängert",12,10,"12x10",335,1]
["XCUW111BR","CU-Schiene FB1 12x10x275mm waagrecht beidseitig um 15mm verlängert",12,10,"12x10",275,1]
["XCUW111E","CU-Schiene FB1 12x10x290mm waagrecht einseitig um 45mm verlängert",12,10,"12x10",290,1]
["XCUW111ER","CU-Schiene FB1 12x10x260mm waagrecht einseitig um 15mm verlängert",12,10,"12x10",260,1]
["XCUW112","CU-Schiene FB2 12x10x495mm waagrecht ohne Überstand",12,10,"12x10",495,1]
["XCUW112B","CU-Schiene FB2 12x10x585mm waagrecht beidseitig um 45mm verlängert",12,10,"12x10",585,1]
["XCUW112BR","CU-Schiene FB2 12x10x525mm waagrecht beidseitig um 15mm verlängert",12,10,"12x10",525,1]
["XCUW112E","CU-Schiene FB2 12x10x540mm waagrecht einseitig um 45mm verlängert",12,10,"12x10",540,1]
["XCUW112ER","CU-Schiene FB2 12x10x510mm waagrecht einseitig um 15mm verlängert",12,10,"12x10",510,1]
["XCUW112K","CU-Schiene FB2 12x10x448mm waagrecht zwischen Trägerprofil",12,10,"12x10",445,1]
["XCUW113","CU-Schiene FB3 12x10x745mm waagrecht ohne Überstand",12,10,"12x10",745,1]
["XCUW113B","CU-Schiene FB3 12x10x835mm waagrecht beidseitig um 45mm verlängert",12,10,"12x10",835,1]
["XCUW113BR","CU-Schiene FB3 12x10x775mm waagrecht beidseitig um 15mm verlängert",12,10,"12x10",774,1]
["XCUW113E","CU-Schiene FB3 12x10x790mm waagrecht einseitig um 45mm verlängert",12,10,"12x10",790,1]
["XCUW113ER","CU-Schiene FB3 12x10x760mm waagrecht einseitig um 15mm verlängert",12,10,"12x10",760,1]
["XCUW113K","CU-Schiene FB3 12x10x698mm waagrecht zwischen Trägerprofil",12,10,"12x10",698,1]
["XCUW114","CU-Schiene FB4 12x10x995mm waagrecht ohne Überstand",12,10,"12x10",995,1]
["XCUW114B","CU-Schiene FB4 12x10x1085mm waagrecht beidseitig um 45mm verlängert",12,10,"12x10",1085,1]
["XCUW114BR","CU-Schiene FB4 12x10x1025mm waagrecht beidseitig um 15mm verlängert",12,10,"12x10",1025,1]
["XCUW114E","CU-Schiene FB4 12x10x1040mm waagrecht einseitig um 45mm verlängert",12,10,"12x10",1040,1]
["XCUW114ER","CU-Schiene FB4 12x10x1010mm waagrecht einseitig um 15mm verlängert",12,10,"12x10",1010,1]
["XCUW115","CU-Schiene FB5 12x10x1245mm waagrecht ohne Überstand",12,10,"12x10",1245,1]
["XCUW115B","CU-Schiene FB5 12x10x1335mm waagrecht beidseitig um 45mm verlängert",12,10,"12x10",1335,1]
["XCUW115BR","CU-Schiene FB5 12x10x1275mm waagrecht beidseitig um 15mm verlängert",12,10,"12x10",1275,1]
["XCUW115E","CU-Schiene FB5 12x10x1290mm waagrecht einseitig um 45mm verlängert",12,10,"12x10",1290,1]
["XCUW115ER","CU-Schiene FB5 12x10x1260mm waagrecht einseitig um 15mm verlängert",12,10,"12x10",1260,1]
["XCUW121","CU-Schiene FB1 20x10x245mm waagrecht ohne Überstand",20,10,"20x10",245,1]
["XCUW121B","CU-Schiene FB1 20x10x337mm waagrecht beidseitig um 46mm verlängert",20,10,"20x10",337,1]
["XCUW121E","CU-Schiene FB1 20x10x291mm waagrecht einseitig um 46mm verlängert",20,10,"20x10",291,1]
["XCUW121K","CU-Schiene FB1 20x10x198mm waagrecht zwischen Trägerprofil",20,10,"20x10",198,1]
["XCUW122","CU-Schiene FB2 20x10x495mm waagrecht ohne Überstand",20,10,"20x10",495,1]
["XCUW122B","CU-Schiene FB2 20x10x587mm waagrecht beidseitig um 46mm verlängert",20,10,"20x10",587,1]
["XCUW122E","CU-Schiene FB2 20x10x541mm waagrecht einseitig um 46mm verlängert",20,10,"20x10",541,1]
["XCUW122K","CU-Schiene FB2 20x10x448mm waagrecht zwischen Trägerprofil",20,10,"20x10",448,1]
["XCUW123","CU-Schiene FB3 20x10x745mm waagrecht kein Überstand",20,10,"20x10",745,1]
["XCUW123B","CU-Schiene FB3 20x10x837mm waagrecht beidseitig um 46mm verlängert",20,10,"20x10",837,1]
["XCUW123E","CU-Schiene FB3 20x10x791mm waagrecht einseitig um 46mm verlängert",20,10,"20x10",791,1]
["XCUW123K","CU-Schiene FB3 20x10x698mm waagrecht zwischen Trägerprofil",20,10,"20x10",698,1]
["XCUW124","CU-Schiene FB4 20x10x995mm waagrecht ohne Überstand",20,10,"20x10",995,1]
["XCUW124B","CU-Schiene FB4 20x10x1087mm waagrecht beidseitig um 46mm verlängert",20,10,"20x10",1087,1]
["XCUW124E","CU-Schiene FB4 20x10x1041mm waagrecht einseitig um 46mm verlängert",20,10,"20x10",1041,1]
["XCUW125","CU-Schiene FB5 20x10x1245mm waagrecht ohne Überstand",20,10,"20x10",1245,1]
["XCUW125B","CU-Schiene FB5 20x10x1337mm waagrecht beidseitig um 46mm verlängert",20,10,"20x10",1337,1]
["XCUW125E","CU-Schiene FB5 20x10x1291mm waagrecht einseitig um 46mm verlängert",20,10,"20x10",1291,1]
["XCUW131","CU-Schiene FB1 30x10x245mm waagrecht ohne Überstand",30,10,"30x10",245,1]
["XCUW131B","CU-Schiene FB1 30x10x337mm waagrecht beidseitig um 46mm verlängert",30,10,"30x10",337,1]
["XCUW131E","CU-Schiene FB1 30x10x291mm waagrecht einseitig um 46mm verlängert",30,10,"30x10",291,1]
["XCUW131K","CU-Schiene FB1 30x10x198mm waagrecht zwischen Trägerprofil",30,10,"30x10",198,1]
["XCUW132","CU-Schiene FB2 30x10x495mm waagrecht ohne Überstand",30,10,"30x10",495,1]
["XCUW132B","CU-Schiene FB2 30x10x587mm waagrecht beidseitig um 46mm verlängert",30,10,"30x10",587,1]
["XCUW132E","CU-Schiene FB2 30x10x541mm waagrecht einseitig um 46mm verlängert",30,10,"30x10",541,1]
["XCUW132K","CU-Schiene FB2 30x10x448mm waagrecht zwischen Trägerprofil",30,10,"30x10",448,1]
["XCUW133","CU-Schiene FB3 30x10x745mm waagrecht ohne Überstand",30,10,"30x10",745,1]
["XCUW133B","CU-Schiene FB3 30x10x837mm waagrecht beidseitig um 46mm verlängert",30,10,"30x10",837,1]
["XCUW133E","CU-Schiene FB3 30x10x791mm waagrecht einseitig um 46mm verlängert",30,10,"30x10",791,1]
["XCUW133K","CU-Schiene FB3 30x10x698mm waagrecht zwischen Trägerprofil",30,10,"30x10",698,1]
["XCUW134B","CU-Schiene FB4 30x10x1087mm waagrecht beidseitig um 46mm verlängert",30,10,"30x10",1087,1]
["XCUW134E","CU-Schiene FB4 30x10x1041mm waagrecht einseitig um 46mm verlängert",30,10,"30x10",1041,1]
["XCUW135","CU-Schiene FB5 30x10x1245mm waagrecht ohne Überstand",30,10,"30x10",1245,1]
["XCUW135B","CU-Schiene FB5 30x10x1337mm waagrecht beidseitig um 46mm verlängert",30,10,"30x10",1337,1]
["XCUW135E","CU-Schiene FB5 30x10x1291mm waagrecht einseitig um 46mm verlängert",30,10,"30x10",1291,1]
["XCUW141","CU-Schiene FB1 40x10x245mm waagrecht ohne Überstand",40,10,"40x10",245,1]
["XCUW141B","CU-Schiene FB1 40x10x337mm waagrecht beidseitig um 46mm verlängert",40,10,"40x10",337,1]
["XCUW141E","CU-Schiene FB1 40x10x291mm waagrecht einseitig um 46mm verlängert",40,10,"40x10",291,1]
["XCUW142","CU-Schiene FB2 40x10x495mm waagrecht ohne Überstand",40,10,"40x10",495,1]
["XCUW142B","CU-Schiene FB2 40x10x587mm waagrecht beidseitig um 46mm verlängert",40,10,"40x10",587,1]
["XCUW142E","CU-Schiene FB2 40x10x541mm waagrecht einseitig um 46mm verlängert",40,10,"40x10",541,1]
["XCUW143","CU-Schiene FB3 40x10x745mm waagrecht ohne Überstand",40,10,"40x10",745,1]
["XCUW143B","CU-Schiene FB3 40x10x837mm waagrecht beidseitig um 46mm verlängert",40,10,"40x10",837,1]
["XCUW143E","CU-Schiene FB3 40x10x791mm waagrecht einseitig um 46mm verlängert",40,10,"40x10",791,1]
["XCUW144E","CU-Schiene FB4 40x10x1041mm waagrecht einseitig um 46mm verlängert",40,10,"40x10",1041,1]
["XCUW145","CU-Schiene FB5 40x10x1245mm waagrecht ohne Überstand",40,10,"40x10",1245,1]
["XCUW145B","CU-Schiene FB5 40x10x1337mm waagrecht beidseitig um 46mm verlängert",40,10,"40x10",1337,1]
["XCUW145E","CU-Schiene FB5 40x10x1291mm waagrecht einseitig um 46mm verlängert",40,10,"40x10",1291,1]
["XCUW151","CU-Schiene FB1 50x10x245mm waagrecht ohne Überstand",50,10,"50x10",245,1]
["XCUW151B","CU-Schiene FB1 50x10x337mm waagrecht beidseitig um 46mm verlängert",50,10,"50x10",337,1]
["XCUW151E","CU-Schiene FB1 50x10x291mm waagrecht einseitig um 46mm verlängert",50,10,"50x10",291,1]
["XCUW152","CU-Schiene FB2 50x10x495mm waagrecht ohne Überstand",50,10,"50x10",495,1]
["XCUW152B","CU-Schiene FB2 50x10x587mm waagrecht beidseitig um 46mm verlängert",50,10,"50x10",587,1]
["XCUW152E","CU-Schiene FB2 50x10x541mm waagrecht einseitig um 46mm verlängert",50,10,"50x10",541,1]
["XCUW153","CU-Schiene FB3 50x10x745mm waagrecht ohne Überstand",50,10,"50x10",745,1]
["XCUW153B","CU-Schiene FB3 50x10x837mm waagrecht beidseitig um 46mm verlängert",50,10,"50x10",837,1]
["XCUW153E","CU-Schiene FB3 50x10x791mm waagrecht einseitig um 46mm verlängert",50,10,"50x10",791,1]
["XCUW154","CU-Schiene FB4 50x10x995mm waagrecht ohne Überstand",50,10,"50x10",995,1]
["XCUW154B","CU-Schiene FB4 50x10x1087mm waagrecht beidseitig um 46mm verlängert",50,10,"50x10",1087,1]
["XCUW154E","CU-Schiene FB4 50x10x1041mm waagrecht einseitig um 46mm verlängert",50,10,"50x10",1041,1]
["XCUW155","CU-Schiene FB5 50x10x1245mm waagrecht ohne Überstand",50,10,"50x10",1245,1]
["XCUW155B","CU-Schiene FB5 50x10x1337mm waagrecht beidseitig um 46mm verlängert",50,10,"50x10",1337,1]
["XCUW155E","CU-Schiene FB5 50x10x1291mm waagrecht einseitig um 46mm verlängert",50,10,"50x10",1291,1]
["XCUW161","CU-Schiene FB1 60x10x245mm waagrecht ohne Überstand",60,10,"60x10",245,1]
["XCUW161B","CU-Schiene FB1 60x10x337mm waagrecht beidseitig um 46mm verlängert",60,10,"60x10",337,1]
["XCUW161E","CU-Schiene FB1 60x10x291mm waagrecht einseitig um 46mm verlängert",60,10,"60x10",291,1]
["XCUW162","CU-Schiene FB2 60x10x495mm waagrecht ohne Überstand",60,10,"60x10",495,1]
["XCUW162B","CU-Schiene FB2 60x10x587mm waagrecht beidseitig um 46mm verlängert",60,10,"60x10",587,1]
["XCUW162E","CU-Schiene FB2 60x10x541mm waagrecht einseitig um 46mm verlängert",60,10,"60x10",541,1]
["XCUW163","CU-Schiene FB3 60x10x745mm waagrecht ohne Überstand",60,10,"60x10",745,1]
["XCUW163B","CU-Schiene FB3 60x10x837mm waagrecht beidseitig um 46mm verlängert",60,10,"60x10",837,1]
["XCUW163E","CU-Schiene FB3 60x10x791mm waagrecht einseitig um 46mm verlängert",60,10,"60x10",791,1]
["XCUW164","CU-Schiene FB4 60x10x995mm waagrecht ohne Überstand",60,10,"60x10",995,1]
["XCUW164B","CU-Schiene FB4 60x10x1087mm waagrecht beidseitig um 46mm verlängert",60,10,"60x10",1087,1]
["XCUW164E","CU-Schiene FB4 60x10x1041mm waagrecht einseitig um 46mm verlängert",60,10,"60x10",1041,1]
["XCUW165","CU-Schiene FB5 60x10x1245mm waagrecht ohne Überstand",60,10,"60x10",1245,1]
["XCUW165B","CU-Schiene FB5 60x10x1337mm waagrecht beidseitig um 46mm verlängert",60,10,"60x10",1337,1]
["XCUW165E","CU-Schiene FB5 60x10x1291mm waagrecht einseitig um 46mm verlängert",60,10,"60x10",1291,1]
["XCUW171","CU-Schiene FB1 80x10x245mm waagrecht ohne Überstand",80,10,"80x10",245,1]
["XCUW172","CU-Schiene FB2 80x10x495mm waagrecht ohne Überstand",80,10,"80x10",495,1]
["XCUW173","CU-Schiene FB3 80x10x745mm waagrecht ohne Überstand",80,10,"80x10",745,1]
["XCUW174","CU-Schiene FB4 80x10x995mm waagrecht ohne Überstand",80,10,"80x10",995,1]
["XCUW175","CU-Schiene FB5 80x10x1245mm waagrecht ohne Überstand",80,10,"80x10",1245,1]
["XCUW181","CU-Schiene FB1 100x10x245mm waagrecht ohne Überstand",100,10,"100x10",245,1]
["XCUW182","CU-Schiene FB2 100x10x495mm waagrecht ohne Überstand",100,10,"100x10",495,1]
["XCUW183","CU-Schiene FB3 100x10x745mm waagrecht ohne Überstand",100,10,"100x10",745,1]
["XCUW184","CU-Schiene FB4 100x10x995mm waagrecht ohne Überstand",100,10,"100x10",995,1]
["XCUW185","CU-Schiene FB5 100x10x1245mm waagrecht ohne Überstand",100,10,"100x10",1245,1]
["XCUW191","CU-Schiene FB1 120x10x245mm waagrecht ohne Überstand",120,10,"120x10",245,1]
["XCUW192","CU-Schiene FB2 120x10x495mm waagrecht ohne Überstand",120,10,"120x10",495,1]
["XCUW193","CU-Schiene FB3 120x10x745mm waagrecht ohne Überstand",120,10,"120x10",745,1]
["XCUW194","CU-Schiene FB4 120x10x995mm waagrecht ohne Überstand",120,10,"120x10",995,1]
["XCUW195","CU-Schiene FB5 120x10x1245mm waagrecht ohne Überstand",120,10,"120x10",1245,1]
["XCUW511","CU-Schiene FB1 12x5x245mm waagrecht ohne Überstand",12,5,"12x5",245,1]
["XCUW511B","CU-Schiene FB1 12x5x335mm waagrecht beidseitig um 45mm verlängert",12,5,"12x5",335,1]
["XCUW511BR","CU-Schiene FB1 12x5x275mm waagrecht beidseitig um 15mm verlängert",12,5,"12x5",275,1]
["XCUW511E","CU-Schiene FB1 12x5x290mm waagrecht einseitig um 45mm verlängert",12,5,"12x5",290,1]
["XCUW511K","CU-Schiene FB1 12x5x198mm waagrecht zwischen Trägerprofil",12,5,"12x5",198,1]
["XCUW512","CU-Schiene FB2 12x5x495mm waagrecht ohne Überstand",12,5,"12x5",495,1]
["XCUW512BR","CU-Schiene FB2 12x5x525mm waagrecht beidseitig um 15mm verlängert",12,5,"12x5",525,1]
["XCUW512ER","CU-Schiene FB2 12x5x510mm waagrecht einseitig um 15mm verlängert",12,5,"12x5",510,1]
["XCUW512K","CU-Schiene FB2 12x5x448mm waagrecht zwischen Trägerprofil",12,5,"12x5",448,1]
["XCUW513","CU-Schiene FB3 12x5x745mm waagrecht ohne Überstand",12,5,"12x5",745,1]
["XCUW513B","CU-Schiene FB3 12x5x835mm waagrecht beidseitig um 45mm verlängert",12,5,"12x5",835,1]
["XCUW513BR","CU-Schiene FB3 12x5x775mm waagrecht beidseitig um 15mm verlängert",12,5,"12x5",775,1]
["XCUW513E","CU-Schiene FB3 12x5x790mm waagrecht einseitig um 45mm verlängert",12,5,"12x5",790,1]
["XCUW513ER","CU-Schiene FB3 12x5x760mm waagrecht einseitig um 15mm verlängert",12,5,"12x5",760,1]
["XCUW513K","CU-Schiene FB3 12x5x698mm waagrecht zwischen Trägerprofil",12,5,"12x5",698,1]
["XCUW514B","CU-Schiene FB4 12x5x1085mm waagrecht beidseitig um 45mm verlängert",12,5,"12x5",1085,1]
["XCUW514BR","CU-Schiene FB4 12x5x1025mm waagrecht beidseitig um 15mm verlängert",12,5,"12x5",1025,1]
["XCUW514E","CU-Schiene FB4 12x5x1040mm waagrecht einseitig um 45mm verlängert",12,5,"12x5",1040,1]
["XCUW514ER","CU-Schiene FB4 12x5x1010mm waagrecht einseitig um 15mm verlängert",12,5,"12x5",1010,1]
["XCUW515","CU-Schiene FB5 12x5x1245mm waagrecht ohne Überstand",12,5,"12x5",1245,1]
["XCUW515B","CU-Schiene FB5 12x5x1335mm waagrecht beidseitig um 45mm verlängert",12,5,"12x5",1335,1]
["XCUW515BR","CU-Schiene FB5 12x5x1275mm waagrecht beidseitig um 15mm verlängert",12,5,"12x5",1275,1]
["XCUW515E","CU-Schiene FB5 12x5x1290mm waagrecht einseitig um 45mm verlängert",12,5,"12x5",1290,1]
["XCUW515ER","CU-Schiene FB5 12x5x1260mm waagrecht einseitig um 15mm verlängert",12,5,"12x5",1260,1]
["XCUW521","CU-Schiene FB1 20x5x245mm waagrecht ohne Überstand",20,5,"20x5",245,1]
["XCUW521B","CU-Schiene FB1 20x5x337mm waagrecht beidseitig um 46mm verlängert",20,5,"20x5",337,1]
["XCUW521E","CU-Schiene FB1 20x5x291mm waagrecht einseitig um 46mm verlängert",20,5,"20x5",291,1]
["XCUW521K","CU-Schiene FB1 20x5x198mm waagrecht zwischen Trägerprofil",20,5,"20x5",198,1]
["XCUW522B","CU-Schiene FB2 20x5x587mm waagrecht beidseitig um 46mm verlängert",20,5,"20x5",587,1]
["XCUW522E","CU-Schiene FB2 20x5x541mm waagrecht einseitig um 46mm verlängert",20,5,"20x5",541,1]
["XCUW522K","CU-Schiene FB2 20x5x448mm waagrecht zwischen Trägerprofil",20,5,"20x5",448,1]
["XCUW523","CU-Schiene FB3 20x5x745mm waagrecht ohne Überstand",20,5,"20x5",745,1]
["XCUW523B","CU-Schiene FB3 20x5x837mm waagrecht beidseitig um 46mm verlängert",20,5,"20x5",837,1]
["XCUW523E","CU-Schiene FB3 20x5x791mm waagrecht einseitig um 46mm verlängert",20,5,"20x5",791,1]
["XCUW523K","CU-Schiene FB3 20x5x698mm waagrecht zwischen Trägerprofil",20,5,"20x5",698,1]
["XCUW524","CU-Schiene FB4 20x5x995mm waagrecht ohne Überstand",20,5,"20x5",995,1]
["XCUW524B","CU-Schiene FB4 20x5x1087mm waagrecht beidseitig um 46mm verlängert",20,5,"20x5",1087,1]
["XCUW524E","CU-Schiene FB4 20x5x1041mm waagrecht einseitig um 46mm verlängert",20,5,"20x5",1041,1]
["XCUW525","CU-Schiene FB5 20x5x1245mm waagrecht ohne Überstand",20,5,"20x5",1245,1]
["XCUW525B","CU-Schiene FB5 20x5x1337mm waagrecht beidseitig um 46mm verlängert",20,5,"20x5",1337,1]
["XCUW525E","CU-Schiene FB5 20x5x1291mm waagrecht einseitig um 46mm verlängert",20,5,"20x5",1291,1]
["XCUW531","CU-Schiene FB1 30x5x245mm waagrecht ohne Überstand",30,5,"30x5",245,1]
["XCUW531B","CU-Schiene FB1 30x5x337mm waagrecht beidseitig um 46mm verlängert",30,5,"30x5",337,1]
["XCUW531E","CU-Schiene FB1 30x5x291mm waagrecht einseitig um 46mm verlängert",30,5,"30x5",291,1]
["XCUW531K","CU-Schiene FB1 30x5x198mm waagrecht zwischen Trägerprofil",30,5,"30x5",198,1]
["XCUW532","CU-Schiene FB2 30x5x495mm waagrecht ohne Überstand",30,5,"30x5",495,1]
["XCUW532B","CU-Schiene FB2 30x5x587mm waagrecht beidseitig um 46mm verlängert",30,5,"30x5",587,1]
["XCUW532E","CU-Schiene FB2 30x5x541mm waagrecht einseitig um 46mm verlängert",30,5,"30x5",541,1]
["XCUW532K","CU-Schiene FB2 30x5x448mm waagrecht zwischen Trägerprofil",30,5,"30x5",448,1]
["XCUW533","CU-Schiene FB3 30x5x745mm waagrecht ohne Überstand",30,5,"30x5",745,1]
["XCUW533B","CU-Schiene FB3 30x5x837mm waagrecht beidseitig um 46mm verlängert",30,5,"30x5",837,1]
["XCUW533E","CU-Schiene FB3 30x5x791mm waagrecht einseitig um 46mm verlängert",30,5,"30x5",791,1]
["XCUW533K","CU-Schiene FB3 30x5x698mm waagrecht zwischen Trägerprofil",30,5,"30x5",698,1]
["XCUW534","CU-Schiene FB4 30x5x995mm waagrecht ohne Überstand",30,5,"30x5",995,1]
["XCUW534B","CU-Schiene FB4 30x5x1087mm waagrecht beidseitig um 46mm verlängert",30,5,"30x5",1087,1]
["XCUW534E","CU-Schiene FB4 30x5x1041mm waagrecht einseitig um 46mm verlängert",30,5,"30x5",1041,1]
["XCUW535","CU-Schiene FB5 30x5x1245mm waagrecht ohne Überstand",30,5,"30x5",1245,1]
["XCUW535B","CU-Schiene FB5 30x5x1337mm waagrecht beidseitig um 46mm verlängert",30,5,"30x5",1337,1]
["XCUW535E","CU-Schiene FB5 30x5x1291mm waagrecht einseitig um 46mm verlängert",30,5,"30x5",1291,1]
["XVGW532F","CU-Schiene vernickelt FB2 30x5mm für SIF mit Befestigungsschrauben",30,5,"30x5",495,1]
["XVGW533F","CU-Schiene vernickelt FB3 30x5mm für SIF mit Befestigungsschrauben",30,5,"30x5",745,1]
["XVGW543F","CU-Schiene vernickelt FB3 40x5mm für SIF mit Befestigungsschrauben",40,5,"40x5",745,1]
["XWL305170N","Wandlerlasche CU vernickelt 30x5x170mm ohne Befestigungsschrauben (3 Stk.)",30,5,"30x5",170,3]
["XWL310250N","Wandlerlasche CU vernickelt 30x10x250mm ohne Befestigungsschrauben (3 Stk.)",30,10,"30x10",250,3]
["XWL410170N","Wandlerlasche CU vernickelt 40x10x170mm ohne Befestigungsschrauben (3 Stk.)",40,10,"40x10",170,3]
["XWL410250N","Wandlerlasche CU vernickelt 40x10x250mm ohne Befestigungsschrauben (3 Stk.)",40,10,"40x10",250,3]
["XWL512250N","Wandlerlasche CU vernickelt 50x12x250mm ohne Befestigungsschrauben (3 Stk.)",50,12,"50x12",250,3]
["XWL812250N","Wandlerlasche CU vernickelt 80x12x250mm 3er Set ohne Befestigungsschrauben",80,12,"80x12",250,3]
["12x5","Sammelschiene 12x5mm",12,5,"12x5",null,1]
["20x5","Sammelschiene 20x5mm",20,5,"20x5",null,1]
["12x10","Sammelschiene 12x10mm",12,10,"12x10",null,1]
["30x5","Sammelschiene 30x5mm",30,5,"30x5",null,1]
["20x10","Sammelschiene 20x10mm",20,10,"20x10",null,1]
["30x10","Sammelschiene 30x10mm",30,10,"30x10",null,1]
["40x10","Sammelschiene 40x10mm",40,10,"40x10",null,1]
["50x10","Sammelschiene 50x10mm",50,10,"50x10",null,1]
["60x10","Sammelschiene 60x10mm",30,10,"60x10",null,1]
["80x10","Sammelschiene 80x10mm",80,10,"80x10",null,1]
["100x10","Sammelschiene 100x10mm",100,10,"100x10",null,1]
["120x10","Sammelschiene 120x10mm",120,10,"120x10",null,1]

{"sheet":"Tabelle 5 - Pv_Kabel","index":5,"n_rows":17,"n_cols":7,"rows_kept":17,"cut":false,"hidden":false,"merged":[]}
["Typ ","Geräteart","Hersteller","Bemerkung","Maximal Strom, Imax / A\n(Kabeltemperatur 70°C)","Verlustleistung des Gerätes pro Pol bei Maximalstrom\nin Watt"]
["1,5 qmm","Kabel H07V-K je 1m","ABN","Lufttemperatur 55°C",15,3.2,"1,5 qmm"]
["2,5qmm","Kabel H07V-K je 1m","ABN","Lufttemperatur 55°C",21,3.7,"2,5qmm"]
["4 qmm","Kabel H07V-K je 1m","ABN","Lufttemperatur 55°C",28,4.2,"4 qmm"]
["6 qmm","Kabel H07V-K je 1m","ABN","Lufttemperatur 55°C",36,4.7,"6 qmm"]
["10 qmm","Kabel H07V-K je 1m","ABN","Lufttemperatur 55°C",50,5.4,"10 qmm"]
["16 qmm","Kabel H07V-K je 1m","ABN","Lufttemperatur 55°C",67,6.2,"16 qmm"]
["25 qmm","Kabel H07V-K je 1m","ABN","Lufttemperatur 55°C",89,6.9,"25 qmm"]
["35 qmm","Kabel H07V-K je 1m","ABN","Lufttemperatur 55°C",110,7.7,"35 qmm"]
["50 qmm","Kabel H07V-K je 1m","ABN","Lufttemperatur 55°C",134,8.3000000000000007,"50 qmm"]
["70 qmm","Kabel H07V-K je 1m","ABN","Lufttemperatur 55°C",171,9.4,"70 qmm"]
["95 qmm","Kabel H07V-K je 1m","ABN","Lufttemperatur 55°C",208,10,"95 qmm"]
["120 qmm","Kabel H07V-K je 1m","ABN","Lufttemperatur 55°C",242,10.7,"120 qmm"]
["150 qmm","Kabel H07V-K je 1m","ABN","Lufttemperatur 55°C",278,11.5,"150 qmm"]
["185 qmm","Kabel H07V-K je 1m","ABN","Lufttemperatur 55°C",318,12,"185 qmm"]
["240 qmm","Kabel H07V-K je 1m","ABN","Lufttemperatur 55°C",374,12.7,"240 qmm"]
["300qmm","Kabel H07V-K je 1m","ABN","Lufttemperatur 55°C",432,13.5,"300 qmm"]

{"sheet":"Legende","index":6,"n_rows":30,"n_cols":2,"rows_kept":30,"cut":false,"hidden":false,"merged":[]}
[]
["Legende:"]
[null,"Die Derating-Kurve beschreibt die maximale zulässige Verlustleistung eines elektrischen oder elektronischen Bauteiles in Abhängigkeit von seiner Umgebungstemperatur."]
[null,"In der Praxis wird die Leistungsreduktion und damit die Berücksichtigung der Derating-Kurve oft nicht vom Bauteil oder Gerät selbst vorgenommen,\nsondern ist Aufgabe des Benutzers, sofern sie nicht bereits bei der Entwicklung des Gesamtproduktes berücksichtigt wurde. "]
[]
[null,"RDF = Bemessungsbelastungsfaktor\nUnter der Voraussetzung, dass die Belastung der Einspeisung deren Bemessungsstrom nicht überschreitet, ist der Belastungsfaktor der Anteil der jeweiligen\nBemessungsströme, den jede Kombination von abgehenden Stromkreisen gleichzeitig und dauerhaft führen kann, ohne die Schaltgerätekombination zu überlasten."]
[]
[]
[]
[null,"Festlegung: Betriebsbedingungen"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"Sammelschienen Verluste für 3-poliges System"]

{"sheet":"Tabelle 101 - (61439-2, -3)","index":7,"n_rows":35,"n_cols":7,"rows_kept":35,"cut":false,"hidden":false,"merged":[[34,1,34,2],[34,5,34,6]]}
["Tabelle Stromkreis - Belastungsfaktor",null,null,null,"Tabelle Stromkreis - Belastungsfaktor"]
[null,null,"DIN EN 61439-2 ; PSC",null,null,null,"DIN EN 61439-3 ; DBO"]
[]
[null,"Anzahl Stromkreise","angenommener\nBelastungsfaktor",null,null,"Anzahl Stromkreise","angenommener\nBelastungsfaktor"]
[null,1,1,null,null,1,1]
[null,2,0.9,null,null,2,0.8]
[null,3,0.9,null,null,3,0.8]
[null,4,0.8,null,null,4,0.7]
[null,5,0.8,null,null,5,0.7]
[null,6,0.7,null,null,6,0.6]
[null,7,0.7,null,null,7,0.6]
[null,8,0.7,null,null,8,0.6]
[null,9,0.7,null,null,9,0.9]
[null,10,0.60000000000000009,null,null,10,0.5]
[null,11,0.60000000000000009,null,null,11,0.5]
[null,12,0.60000000000000009,null,null,12,0.5]
[null,13,0.60000000000000009,null,null,13,0.5]
[null,14,0.60000000000000009,null,null,14,0.5]
[null,15,0.60000000000000009,null,null,15,0.5]
[null,16,0.60000000000000009,null,null,16,0.5]
[null,17,0.60000000000000009,null,null,17,0.5]
[null,18,0.60000000000000009,null,null,18,0.5]
[null,19,0.60000000000000009,null,null,19,0.5]
[null,20,0.60000000000000009,null,null,20,0.5]
[null,21,0.6,null,null,21,0.5]
[null,22,0.6,null,null,22,0.5]
[null,23,0.6,null,null,23,0.5]
[null,24,0.6,null,null,24,0.5]
[null,25,0.6,null,null,25,0.5]
[null,26,0.6,null,null,26,0.5]
[null,27,0.6,null,null,27,0.5]
[null,28,0.6,null,null,28,0.5]
[null,29,0.6,null,null,29,0.5]
[null,30,0.6,null,null,30,0.5]
["Erläuterung:","Durch gegenseitige Erwärmung der Einbaugeräte\nmuss eine Leistungsreduzierung in Form\neines Belastungsfaktors bestimmt werden.",null,null,"Erläuterung:","Durch gegenseitige Erwärmung der Einbaugeräte\nmuss eine Leistungsreduzierung in Form\neines Belastungsfaktors bestimmt werden."]